## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2025-12-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | 0.03 | 0.03 | NF | 0.02 | NF | NF | 0.04 | 1467 | 0.75 | 191.7164 | 143.7873 | 12.4 | 7.41 | 18.508 | Y |  | 5
2 | NF | NF | 0.03 | 0.03 | 0.03 | 0.03 | 0.06 | 1504 | 0.71 | 187 | 132.77 | 12.4 | 7.29 | 17.6825 | Y |  | 5
3 | 0.03 | NF | NF | 0.03 | 0.03 | 0.03 | 0.04 | 1501 | 0.73 | 187.3738 | 136.7828 | 14 | 7.45 | 16.6812 | Y |  | 5
4 | NF | NF | NF | 0.05 | 0.04 | 0.03 | 0.07 | 1512 | 0.68 | 186.0106 | 126.4872 | 14.7 | 7.4 | 15.5402 | Y |  | 5
5 | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.09 | 1793 | 0.7 | 156.8589 | 109.8012 | 11.4 | 7.45 | 19.914 | Y |  | 5
6 | NF | NF | NF | 0.03 | NF | NF | 0.05 | 1803 | 0.69 | 155.9889 | 107.6323 | 11.9 | 7.4 | 18.9247 | Y |  | 5
7 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.07 | 1801 | 0.72 | 156.1621 | 112.4367 | 12.4 | 7.43 | 18.5742 | Y |  | 5
8 | 0.03 | 0.03 | 0.03 | NF | 0.02 | NF | 0.06 | 1763 | 0.63 | 159.5281 | 100.5027 | 11.1 | 7.35 | 19.4617 | Y |  | 5
9 | NF | NF | NF | 0.03 | 0.03 | NF | 0.09 | 1802 | 0.53 | 156.0755 | 82.72 | 11 | 7.44 | 19.9864 | Y |  | 5
10 | NF | NF | 0.08 | 0.03 | 0.03 | NF | 0.08 | 1511 | 0.69 | 186.1337 | 128.4322 | 12.8 | 7.54 | 18.5932 | Y |  | 5
11 | NF | NF | 0.03 | 0.03 | 0.03 | 0.05 | 0.08 | 1817 | 0.89 | 154.787 | 137.7604 | 12 | 7.4 | 19.2248 | Y |  | 5
12 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.02 | 0.05 | 1565 | 0.89 | 179.7112 | 159.943 | 12.3 | 7.41 | 18.9195 | Y |  | 5
13 | 0.02 | 0.03 | 0.02 | NF | 0.03 | 0.02 | 0.07 | 1547 | 0.8 | 181.8022 | 145.4418 | 12 | 7.43 | 19.232 | Y |  | 5
14 | NF | NF | NF | 0.03 | 0.03 | 0.02 | 0.07 | 1565 | 0.76 | 179.7112 | 136.5805 | 11.7 | 7.34 | 18.9249 | Y |  | 5
15 | NF | NF | NF | 0.03 | 0.02 | NF | 0.09 | 1561 | 0.75 | 180.1717 | 135.1288 | 12 | 7.41 | 18.9936 | Y |  | 5
16 | NF | NF | NF | 0.02 | 0.03 | 0.03 | 0.14 | 1538 | 0.73 | 182.8661 | 133.4922 | 11.8 | 7.41 | 19.199 | Y |  | 5
17 | 0.03 | NF | NF | NF | 0.02 | 0.03 | 0.08 | 1571 | 0.76 | 179.0248 | 136.0589 | 11.9 | 7.43 | 19.2714 | Y |  | 5
18 | 0.03 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.05 | 1557 | 0.79 | 180.6346 | 142.7013 | 12 | 7.43 | 19.2106 | Y |  | 5
19 | NF | 0.02 | 0.03 | 0.03 | 0.03 | NF | 0.05 | 1358 | 0.81 | 207.1046 | 167.7547 | 11.7 | 7.56 | 20.5412 | Y |  | 5
20 | NF | NF | NF | 0.03 | 0.03 | 0.02 | 0.05 | 1510 | 0.7 | 186.257 | 130.3799 | 12 | 7.34 | 18.438 | Y |  | 5
21 | 0.02 | NF | NF | 0.02 | 0.03 | 0.02 | 0.06 | 1511 | 0.72 | 186.1337 | 134.0163 | 11.5 | 7.38 | 19.3531 | Y |  | 5
22 | 0.02 | NF | NF | 0.03 | 0.03 | NF | 0.04 | 1509 | 0.77 | 186.3804 | 143.5129 | 11.6 | 7.41 | 19.5371 | Y |  | 5
23 | NF | NF | 0.03 | 0.03 | 0.03 | 0.02 | 0.05 | 1509 | 0.7 | 186.3804 | 130.4663 | 12.9 | 7.54 | 18.491 | Y |  | 5
24 | 0.02 | 0.02 | NF | 0.03 | 0.03 | NF | 0.07 | 1477 | 0.72 | 190.4184 | 137.1013 | 11 | 7.45 | 20.4872 | Y |  | 5
25 | NF | NF | NF | 0.03 | 0.03 | 0.04 | 0.08 | 1504 | 0.62 | 187 | 115.94 | 12.5 | 7.44 | 18.1357 | Y |  | 5
26 | 0.03 | 0.02 | 0.02 | 0.07 | 0.03 | 0.03 | 0.07 | 1490 | 0.74 | 188.757 | 139.6802 | 11 | 7.55 | 21.2636 | Y |  | 5
27 | 0.03 | NF | NF | NF | 0.05 | 0.02 | 0.08 | 1503 | 0.61 | 187.1244 | 114.1459 | 11.6 | 7.59 | 20.4305 | Y |  | 5
28 | 0.02 | NF | NF | NF | 0.02 | 0.02 | 0.07 | 1505 | 0.72 | 186.8757 | 134.5505 | 10.9 | 7.59 | 21.6573 | Y |  | 5
29 | 0.02 | NF | NF | NF | 0.02 | 0.03 | 0.07 | 1504 | 0.71 | 187 | 132.77 | 11.1 | 7.52 | 20.8335 | Y |  | 5
30 | NF | NF | NF | NF | 0.02 | 0.02 | 0.07 | 1495 | 0.71 | 188.1258 | 133.5693 | 10.9 | 7.58 | 21.5572 | Y |  | 5
31 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | NF | 0.05 | 1490 | 0.7 | 188.757 | 132.1299 | 10.9 | 7.53 | 21.1589 | Y |  | 5
AVG. | 0.025625 | 0.025 | 0.031667 | 0.030833 | 0.027931 | 0.026667 | 0.067419 | 1565.9032 | 0.72355 | 180.5765 | 130.7896 | 11.9161 | 7.4484 | 19.3138
MAX. | 0.03 | 0.03 | 0.08 | 0.07 | 0.05 | 0.05 | 0.14 | 1817
MIN | Conventional Filtration | [7 empty] | 0.53
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar T Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2026-01-01
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561