## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2026-01-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | NF | NF | NF | NF | 0.03 | 0.02 | 0.06 | 1498 | 0.69 | 187.749 | 129.5468 | 10.2 | 7.63 | 22.926 | Y |  | 5
2 | 0.02 | 0.02 | 0.02 | 0.02 | NF | 0.04 | 0.05 | 1500 | 0.74 | 187.4987 | 138.749 | 10.5 | 7.52 | 21.7449 | Y |  | 5
3 | NF | NF | NF | 0.03 | 0.03 | 0.02 | 0.06 | 1505 | 0.71 | 186.8757 | 132.6818 | 11.1 | 7.64 | 21.7278 | Y |  | 5
4 | 0.02 | NF | NF | 0.03 | 0.02 | NF | 0.05 | 1500 | 0.78 | 187.4987 | 146.249 | 11 | 7.52 | 21.1363 | Y |  | 5
5 | NF | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.08 | 1505 | 0.78 | 186.8757 | 145.7631 | 10.6 | 7.64 | 22.6355 | Y |  | 5
6 | NF | NF | NF | NF | 0.04 | 0.02 | 0.06 | 1498 | 0.74 | 187.749 | 138.9343 | 11.4 | 7.7 | 21.8298 | Y |  | 5
7 | 0.02 | NF | NF | NF | 0.02 | 0.02 | 0.05 | 1512 | 0.73 | 186.0106 | 135.7877 | 10.8 | 7.65 | 22.2905 | Y |  | 5
8 | 0.02 | NF | NF | 0.02 | 0.02 | 0.02 | 0.04 | 1516 | 0.74 | 185.5198 | 137.2846 | 10.3 | 7.66 | 23.1481 | Y |  | 5
9 | NF | NF | NF | 0.02 | 0.02 | 0.03 | 0.05 | 1509 | 0.71 | 186.3804 | 132.3301 | 10.6 | 7.59 | 22.065 | Y |  | 5
10 | 0.04 | NF | NF | NF | 0.05 | 0.03 | 0.08 | 1472 | 0.67 | 191.0652 | 128.0137 | 10.4 | 7.2 | 19.4227 | Y |  | 5
11 | 0.04 | NF | NF | NF | 0.03 | 0.03 | 0.08 | 1507 | 0.68 | 186.6277 | 126.9069 | 10.5 | 7.32 | 20.1402 | Y |  | 5
12 | 0.03 | NF | NF | 0.06 | 0.03 | 0.03 | 0.06 | 1808 | 0.69 | 155.5575 | 107.3347 | 10.4 | 7.42 | 21.0159 | Y |  | 5
13 | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF |  | 5
14 | NF | 0.06 | 0.04 | 0.02 | 0.03 | 0.02 | 0.08 | 1808 | 0.62 | 155.5575 | 96.4457 | 9.8 | 7.4 | 21.5383 | Y |  | 5
15 | 0.03 | 0.03 | 0.02 | NF | NF | 0.02 | 0.06 | 1790 | 0.7 | 157.1218 | 109.9853 | 9.2 | 7.4 | 22.6117 | Y |  | 5
16 | 0.03 | NF | NF | NF | 0.03 | 0.02 | 0.04 | 1795 | 0.67 | 156.6841 | 104.9784 | 9.6 | 7.35 | 21.5655 | Y |  | 5
17 | 0.03 | 0.02 | NF | NF | 0.03 | 0.04 | 0.05 | 1791 | 0.68 | 157.0341 | 106.7832 | 8.9 | 7.55 | 24.2686 | Y |  | 5
18 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.05 | 1803 | 0.68 | 155.9889 | 106.0725 | 10.2 | 7.42 | 21.2699 | Y |  | 5
19 | NF | NF | NF | 0.04 | 0.03 | 0.02 | 0.04 | 1800 | 0.67 | 156.2489 | 104.6868 | 9.7 | 7.46 | 22.2681 | Y |  | 5
20 | NF | NF | NF | 0.03 | 0.02 | 0.03 | 0.04 | 1801 | 0.63 | 156.1621 | 98.3821 | 10.4 | 7.48 | 21.3176 | Y |  | 5
21 | 0.02 | NF | NF | 0.03 | 0.03 | 0.03 | 0.06 | 1802 | 0.65 | 156.0755 | 101.4491 | 10 | 7.38 | 21.1799 | Y |  | 5
22 | 0.02 | NF | NF | NF | 0.03 | 0.03 | 0.05 | 1799 | 0.64 | 156.3357 | 100.0549 | 10.2 | 7.37 | 20.8073 | Y |  | 5
23 | 0.03 | 0.03 | NF | NF | 0.03 | 0.03 | 0.05 | 1789 | 0.54 | 157.2096 | 84.8932 | 10 | 7.42 | 21.2144 | Y |  | 5
24 | 0.03 | NF | NF | 0.03 | 0.03 | 0.03 | 0.04 | 1808 | 0.56 | 155.5575 | 87.1122 | 10.7 | 7.39 | 20.0975 | Y |  | 5
25 | 0.03 | NF | NF | 0.03 | 0.03 | 0.03 | 0.07 | 1815 | 0.57 | 154.9576 | 88.3258 | 9.4 | 7.37 | 21.7586 | Y |  | 5
26 | 0.03 | NF | NF | NF | 0.03 | 0.03 | 0.04 | 1801 | 0.62 | 156.1621 | 96.8205 | 9.5 | 7.38 | 21.8145 | Y |  | 5
27 | 0.02 | NF | NF | 0.03 | 0.02 | NF | 0.04 | 1793 | 0.6 | 156.8589 | 94.1153 | 9.4 | 7.4 | 22.0638 | Y |  | 5
28 | NF | NF | NF | 0.03 | 0.02 | 0.02 | 0.04 | 1798 | 0.6 | 156.4227 | 93.8536 | 9.8 | 7.53 | 22.4946 | Y |  | 5
29 | 0.02 | NF | NF | 0.03 | 0.02 | 0.02 | 0.03 | 1798 | 0.59 | 156.4227 | 92.2894 | 10.4 | 7.62 | 22.2911 | Y |  | 5
30 | 0.02 | NF | NF | NF | 0.02 | 0.02 | 0.03 | 1800 | 0.59 | 156.2489 | 92.1868 | 9.1 | 7.57 | 23.8719 | Y |  | 5
31 | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF |  | 5
AVG. | 0.026316 | 0.03 | 0.025 | 0.029412 | 0.027407 | 0.026296 | 0.052759 | 1686.931 | 0.66448 | 168.0157 | 112.3454 | 10.1414 | 7.4821 | 21.8109
MAX. | 0.04 | 0.06 | 0.04 | 0.06 | 0.05 | 0.04 | 0.08 | 1815
MIN | Conventional Filtration | [7 empty] | 0.54
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar T Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2026-03-03
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561