## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2026-02-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.09 | 1821 | 0.72 | 154.447 | 111.2018 | 9.6 | 7.55 | 23.2707 | Y |  | 5
2 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 1793 | 0.83 | 156.8589 | 130.1929 | 9.5 | 7.61 | 24.2307 | Y |  | 5
3 | 0.02 | NF | 0.03 | NF | NF | 0.02 | 0.04 | 1548 | 0.75 | 181.6848 | 136.2636 | 10.6 | 7.65 | 22.6384 | Y |  | 5
4 | 0.03 | 0.03 | NF | 0.02 | 0.03 | NF | 0.03 | 1552 | 0.8 | 181.2165 | 144.9732 | 13 | 7.62 | 19.1345 | Y |  | 5
5 | NF | NF | NF | 0.03 | 0.02 | 0.02 | 0.04 | 1557 | 0.61 | 180.6346 | 110.1871 | 10.9 | 7.58 | 21.3157 | Y |  | 5
6 | 0.02 | NF | NF | NF | 0.03 | 0.02 | 0.03 | 1558 | 0.74 | 180.5186 | 133.5838 | 10.7 | 7.5 | 21.3105 | Y |  | 5
7 | 0.02 | NF | NF | 0.03 | 0.02 | NF | 0.04 | 1545 | 0.8 | 182.0375 | 145.63 | 9.8 | 7.64 | 23.9238 | Y |  | 5
8 | NF | NF | NF | 0.03 | 0.03 | 0.02 | 0.03 | 1553 | 0.8 | 181.0998 | 144.8798 | 11 | 7.61 | 21.8632 | Y |  | 5
9 | 0.02 | NF | NF | 0.03 | 0.03 | 0.02 | 0.03 | 1547 | 0.79 | 181.8022 | 143.6237 | 10.8 | 7.67 | 22.601 | Y |  | 5
10 | NF | NF | NF | 0.03 | 0.02 | NF | 0.03 | 1561 | 0.79 | 180.1717 | 142.3356 | 14.1 | 7.57 | 17.4407 | Y |  | 5
11 | NF | NF | NF | 0.03 | 0.02 | 0.02 | 0.04 | 1560 | 0.76 | 180.2872 | 137.0183 | 10 | 7.58 | 23.0073 | Y |  | 5
12 | 0.02 | 0.03 | NF | NF | 0.02 | NF | 0.03 | 1547 | 0.81 | 181.8022 | 147.2598 | 11.1 | 7.58 | 21.5164 | Y |  | 5
13 | NF | NF | 0.04 | 0.02 | 0.02 | 0.02 | 0.05 | 1552 | 0.74 | 181.2165 | 134.1002 | 10.1 | 7.59 | 22.8842 | Y |  | 5
14 | NF | NF | NF | 0.03 | 0.03 | 0.02 | 0.05 | 1555 | 0.65 | 180.8669 | 117.5635 | 10.3 | 7.62 | 22.5918 | Y |  | 5
15 | NF | NF | NF | 0.03 | 0.02 | 0.02 | 0.06 | 1157 | 0.73 | 243.0838 | 177.4512 | 11 | 7.59 | 21.5395 | Y |  | 5
16 | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF |  | 5
17 | NF | NF | 0.02 | 0.03 | 0.02 | 0.02 | 0.05 | 1567 | 0.72 | 179.4818 | 129.2269 | 10 | 7.61 | 23.1471 | Y |  | 5
18 | 0.02 | 0.03 | 0.02 | 0.02 | NF | NF | 0.03 | 1551 | 0.79 | 181.3333 | 143.2533 | 10 | 7.62 | 23.4146 | Y |  | 5
19 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.04 | 1559 | 0.71 | 180.4028 | 128.086 | 9.2 | 7.45 | 23.0403 | Y |  | 5
20 | 0.02 | NF | NF | 0.02 | 0.03 | 0.03 | 0.04 | 1551 | 0.66 | 181.3333 | 119.68 | 9.8 | 7.55 | 22.8083 | Y |  | 5
21 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.04 | 1553 | 0.74 | 181.0998 | 134.0139 | 9.9 | 7.59 | 23.1896 | Y |  | 5
22 | NF | NF | NF | 0.02 | 0.03 | 0.02 | 0.04 | 1156 | 0.74 | 243.2941 | 180.0376 | 9.8 | 7.61 | 23.5097 | Y |  | 5
23 | NF | NF | 0.02 | 0.02 | NF | NF | 0.04 | 1550 | 0.76 | 181.4503 | 137.9022 | 10.2 | 7.68 | 23.5211 | Y |  | 5
24 | NF | NF | 0.03 | 0.02 | 0.03 | 0.03 | 0.07 | 1507 | 0.76 | 186.6277 | 141.8371 | 9.5 | 7.71 | 24.9075 | Y |  | 5
25 | 0.03 | 0.05 | NF | NF | 0.03 | 0.04 | 0.08 | 1497 | 0.67 | 187.8744 | 125.8759 | 10 | 7.67 | 23.5095 | Y |  | 5
26 | NF | NF | NF | 0.03 | 0.03 | 0.02 | 0.09 | 1504 | 0.66 | 187 | 123.42 | 9.9 | 7.81 | 24.8438 | Y |  | 5
27 | 0.02 | 0.02 | 0.02 | NF | 0.03 | 0.02 | 0.04 | 1489 | 0.74 | 188.8838 | 139.774 | 11.1 | 7.58 | 21.3474 | Y |  | 5
28 | NF | NF | NF | NF | 0.03 | 0.03 | 0.04 | 1493 | 0.57 | 188.3778 | 107.3753 | 10.5 | 7.59 | 21.8626 | Y |  | 5
AVG. | 0.021818 | 0.03 | 0.02625 | 0.024762 | 0.025 | 0.022381 | 0.045185 | 1532.7037 | 0.73481 | 184.9958 | 135.8054 | 10.4593 | 7.6085 | 22.5322
MAX. | 0.03 | 0.05 | 0.04 | 0.03 | 0.03 | 0.04 | 0.09 | 1821
MIN | Conventional Filtration | [7 empty] | 0.57
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar T Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2026-03-03
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561