## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form County: Linn Conventional Filtration
Sweet Home, City of |  |  |  | I.D. # OR4100851 |  |  | WTP: WTP-B |  | Month of | 2026-03-01 |  |  |  | Required Log inactivation: |  | 0.5
| TURBIDITY | [5 empty] | Highest | Peak Hourly | Min.Cl2 Res. | CONTACT | ACTUAL | TEMP |  | REQ. | CT | log *
| 12AM | 4AM | 8AM | NOON | 4PM | 8PM | Reading of Day 1 | Demand Flow | at 1st user | TIME | (CT) |  | pH | CT | MET? | inacti-
DATE | NTU | NTU | NTU | NTU | NTU | NTU | (NTU) | (gpm) | Mg/L (C)3 | MIN. (T) | C X T | Co |  | Formula | Y / N | vation
1 | 0.02 | NF | NF | NF | 0.03 | 0.02 | 0.04 | 1495 | 0.72 | 188.1258 | 135.4505 | 10.5 | 7.53 | 21.7722 | Y |  | 5
2 | 0.03 | NF | NF | NF | 0.03 | 0.03 | 0.04 | 1486 | 0.7 | 189.2651 | 132.4856 | 12.8 | 7.67 | 19.5283 | Y |  | 5
3 | NF | NF | 0.03 | 0.02 | NF | NF | 0.04 | 1486 | 0.76 | 189.2651 | 143.8415 | 12.1 | 7.58 | 20.0385 | Y |  | 5
4 | NF | NF | NF | 0.02 | 0.02 | 0.02 | 0.04 | 1498 | 0.7 | 187.749 | 131.4243 | 11.1 | 7.66 | 21.8563 | Y |  | 5
5 | 0.02 | 0.03 | NF | NF | NF | NF | 0.06 | 1473 | 0.78 | 190.9355 | 148.9297 | 12.7 | 7.64 | 19.6192 | Y |  | 5
6 | 0.03 | 0.03 | 0.02 | 0.02 | NF | 0.02 | 0.04 | 1488 | 0.8 | 189.0108 | 151.2086 | 11.2 | 7.69 | 22.1921 | Y |  | 5
7 | 0.02 | NF | NF | NF | 0.02 | 0.02 | 0.04 | 1473 | 0.95 | 190.9355 | 181.3887 | 11.4 | 7.65 | 21.9643 | Y |  | 5
8 | NF | NF | 0.02 | NF | 0.03 | 0.03 | 0.04 | 1494 | 0.9 | 188.2517 | 169.4265 | 11 | 7.65 | 22.425 | Y |  | 5
9 | 0.03 | NF | NF | NF | 0.04 | 0.02 | 0.04 | 1503 | 0.92 | 187.1244 | 172.1545 | 13.4 | 7.83 | 20.408 | Y |  | 5
10 | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF |  | 5
11 | NF | NF | 0.02 | 0.02 | 0.02 | 0.02 | 0.04 | 1495 | 0.86 | 188.1258 | 161.7881 | 10.8 | 7.81 | 23.9375 | Y |  | 5
12 | 0.02 | 0.02 | 0.02 | NF | NF | 0.02 | 0.03 | 1477 | 0.93 | 190.4184 | 177.0891 | 10.4 | 7.76 | 24.3449 | Y |  | 5
13 | NF | NF | NF | NF | 0.02 | 0.02 | 0.04 | 1493 | 0.88 | 188.3778 | 165.7724 | 11 | 7.56 | 21.6775 | Y |  | 5
14 | 0.02 | NF | NF | 0.02 | 0.02 | 0.02 | 0.04 | 1486 | 0.9 | 189.2651 | 170.3386 | 11 | 7.64 | 22.3462 | Y |  | 5
15 | NF | NF | NF | NF | 0.03 | 0.03 | 0.04 | 1484 | 0.87 | 189.5202 | 164.8826 | 11.5 | 7.65 | 21.624 | Y |  | 5
16 | 0.02 | 0.02 | NF | NF | 0.03 | 0.03 | 0.03 | 1486 | 0.81 | 189.2651 | 153.3048 | 12 | 7.64 | 20.7119 | Y |  | 5
17 | NF | NF | NF | NF | 0.03 | 0.02 | 0.04 | 1484 | 0.84 | 189.5202 | 159.197 | 12.4 | 7.83 | 21.6351 | Y |  | 5
18 | 0.02 | 0.02 | NF | NF | NF | 0.02 | 0.03 | 1480 | 0.9 | 190.0324 | 171.0292 | 11.3 | 7.71 | 22.4543 | Y |  | 5
19 | 0.02 | NF | NF | NF | NF | 0.02 | 0.04 | 1492 | 0.92 | 188.504 | 173.4237 | 11.3 | 7.81 | 23.3139 | Y |  | 5
20 | 0.02 | 0.02 | 0.02 | NF | 0.03 | 0.03 | 0.06 | 1470 | 0.92 | 191.3252 | 176.0192 | 11.6 | 7.76 | 22.4553 | Y |  | 5
21 | NF | NF | NF | 0.03 | 0.02 | 0.02 | 0.03 | 1484 | 0.89 | 189.5202 | 168.673 | 11.1 | 7.64 | 22.174 | Y |  | 5
22 | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF | NF |  | 5
23 | NF | NF | NF | 0.03 | 0.02 | 0.03 | 0.04 | 1496 | 0.85 | 188 | 159.8 | 11.7 | 7.74 | 21.9764 | Y |  | 5
24 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | NF | 0.03 | 1484 | 0.92 | 189.5202 | 174.3586 | 12.3 | 7.89 | 22.4445 | Y |  | 5
25 | NF | NF | NF | 0.03 | 0.06 | NF | 0.06 | 1489 | 0.91 | 188.8838 | 171.8843 | 12.8 | 7.73 | 20.4453 | Y |  | 5
26 | NF | NF | NF | NF | NF | 0.07 | 0.08 | 1493 | 0.9 | 188.3778 | 169.54 | 11.2 | 7.45 | 20.6328 | Y |  | 5
27 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.04 | 1490 | 0.86 | 188.757 | 162.3311 | 12 | 7.81 | 22.1075 | Y |  | 5
28 | 0.03 | NF | NF | NF | NF | 0.03 | 0.04 | 1478 | 0.87 | 190.2896 | 165.5519 | 12.2 | 7.86 | 22.2298 | Y |  | 5
29 | 0.03 | 0.03 | NF | NF | 0.04 | 0.03 | 0.06 | 1476 | 0.76 | 190.5474 | 144.816 | 12.4 | 7.82 | 21.3659 | Y |  | 5
30 | 0.03 | NF | NF | NF | NF | NF | 0.05 | 1469 | 0.87 | 191.4554 | 166.5662 | 13.2 | 7.95 | 21.4921 | Y |  | 5
31 | NF | NF | NF | 0.03 | 0.03 | 0.03 | 0.04 | 1494 | 0.83 | 188.2517 | 156.2489 | 12.2 | 7.84 | 21.9745 | Y |  | 5
AVG. | 0.023529 | 0.024444 | 0.0225 | 0.024545 | 0.0285 | 0.025833 | 0.042759 | 1486.069 | 0.85241 | 189.2628 | 161.3422 | 11.7448 | 7.7172 | 21.7637
MAX. | 0.03 | 0.03 | 0.03 | 0.03 | 0.06 | 0.07 | 0.08 | 1503
MIN | Conventional Filtration | [7 empty] | 0.7
95% of 4 hr turbidity readings </= 0.3 NTU? Y | [5 empty] | All turbidity readings < IFE2 triggers? Y |  |  |  |  | CT's met everyday? Yes |  |  | All Cl2 Residual at entry point
All the 4 hr turbidity readings </= 1.0 NTU? Y | [13 empty] | >/= 0.2 mg/L Yes
1 Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in Columns "12am through 8pm" may not correspond to continuous readings maximum.
2 IFE = Individual Filter Effluent | [7 empty] | Name (Printed): | Jaegar Howatt |  |  | Signature:
3 If Cl2 at entry point <0.2 mg/l, or CT not met, notify DWP by end of next business day. | [7 empty] | Operator Cert. #: | T-448091 |  |  | Date: | 2026-04-01
4 NF=No Flow | [7 empty] | Phone #: | 541-570-7561