## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Feb_21
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
2 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
3 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
4 | 0.02 | 0.2 | 0.02 | 0.2 | OFF | OFF | 0.02
5 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
6 | 0.02 | OFF | 0.02 | 0.02 | 0.03 | OFF | 0.03
7 | 0.03 | OFF | 0.03 | 0.02 | 0.02 | OFF | 0.03
8 | 0.02 | OFF | OFF | OFF | OFF | 0.024514 | 0.02
9 | OFF | 0.02 | OFF | OFF | OFF | 0.02 | 0.02
10 | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02
11 | OFF | 0.03 | 0.03 | 0.02 | 0.02 | OFF | 0.03
12 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
13 | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
14 | OFF | 0.02 | 0.02 | 0.03 | 0.02 | OFF | 0.03
15 | 0.02 | OFF | 0.02 | 0.024887 | OFF | 0.02 | 0.02
16 | OFF | 0.02 | 0.024219 | 0.024887 | OFF | 0.02 | 0.02
17 | 0.024749 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
18 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
19 | 0.02 | 0.02 | OFF | 0.02 | OFF | 0.02 | 0.02
20 | OFF | OFF | 0.02 | OFF | OFF | 0.02 | 0.02
21 | OFF | OFF | 0.02 | OFF | OFF | OFF | 0.02
22 | 0.02 | OFF | OFF | 0.02 | OFF | 0.02 | 0.02
23 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
24 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
25 | 0.02 | 0.02 | OFF | OFF | OFF | OFF | 0.02
26 | 0.02 | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02
27 | OFF | 0.02 | OFF | OFF | 0.02 | 0.02 | 0.02
28 | OFF | 0.034897 | 0.02 | OFF | 0.02 | 0.02 | 0.02
29
30
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Ricardo R. Saavedra
[5 empty] | SIGNATURE: Ricardo R. Saavedra |  |  | DATE:03/05/2021
[5 empty] | PHONE #: (541) 336-2610 |  |  | CERT #: T-09181
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Feb_21 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 8:00 | 0.84 | 111 | 93.24 | 9.2 | 7.47 | 23.5491 | YES | 883
2 / 8:00 | 0.83 | 111 | 92.13 | 9.1 | 7.46 | 23.5955 | YES | 915
3 / 8:00 | 0.83 | 111 | 92.13 | 9.8 | 7.42 | 22.2105 | YES | 812
4 / 8:00 | 0.82 | 111 | 91.02 | 9 | 7.44 | 23.5584 | YES | 786
5 / 8:00 | 0.82 | 111 | 91.02 | 9 | 7.32 | 22.5806 | YES | 808
6 / 16:00 | 0.82 | 111 | 91.02 | 9 | 7.43 | 23.4751 | YES | 838
7 / 8:00 | 0.81 | 111 | 89.91 | 9 | 7.35 | 22.7949 | YES | 840
8 / 20:00 | 0.79 | 111 | 87.69 | 9 | 7.36 | 22.8237 | YES | 865
9 / 4:00 | 0.78 | 111 | 86.58 | 8 | 7.37 | 24.4505 | YES | 869
10 / 4:00 | 0.78 | 111 | 86.58 | 9 | 7.3 | 22.3207 | YES | 872
11 / 8:00 | 0.77 | 111 | 85.47 | 9 | 7.25 | 21.9069 | YES | 804
12 / 4:00 | 0.77 | 111 | 85.47 | 8 | 7.18 | 22.8336 | YES | 831
13 / 4:00 | 0.77 | 111 | 85.47 | 8 | 7.41 | 24.7724 | YES | 818
14 / 8:00 | 0.8 | 111 | 88.8 | 9 | 7.54 | 24.3531 | YES | 894
15 / 20:00 | 0.83 | 111 | 92.13 | 9 | 7.76 | 26.4307 | YES | 887
16 / 4:00 | 0.83 | 111 | 92.13 | 9 | 7.62 | 25.1421 | YES | 883
17 / 12:00 | 0.82 | 111 | 91.02 | 9.7 | 7.64 | 24.1385 | YES | 849
18 / 20:00 | 0.76 | 111 | 84.36 | 9.7 | 7.48 | 22.6552 | YES | 810
19 / 20:00 | 0.77 | 111 | 85.47 | 9.6 | 7.36 | 21.8869 | YES | 798
20 / 20:00 | 0.76 | 111 | 84.36 | 9.4 | 7.36 | 22.1526 | YES | 839
21 / 8:00 | 0.75 | 111 | 83.25 | 9.4 | 7.35 | 22.0498 | YES | 894
22 / 12:00 | 0.76 | 111 | 84.36 | 9.5 | 7.2 | 20.8068 | YES | 888
23 / 20:00 | 0.76 | 111 | 84.36 | 9.5 | 7.21 | 20.8796 | YES | 864
24 / 4:00 | 0.75 | 111 | 83.25 | 9 | 7.2 | 21.4772 | YES | 801
25 / 4:00 | 0.79 | 111 | 87.69 | 9.1 | 7.1 | 20.6959 | YES | 829
26 / 8:00 | 0.77 | 111 | 85.47 | 9.1 | 7.1 | 20.6495 | YES | 831
27 / 20:00 | 0.77 | 111 | 85.47 | 9.3 | 7.21 | 21.1793 | YES | 838
28 / 16:00 | 0.77 | 111 | 85.47 | 9.3 | 7.25 | 21.4782 | YES | 805
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Feb | 0.029048 | 999.99 | 0.026516 | 0.028812 | 999.99 | 999.99 | 12 | 0 | 0.029637 | 0.86157 | 999.99 | 0.8455 | 0.85492 | 999.99 | 999.99 | 8 | 0.8455 | 0.85
2 | Feb | 0.02893 | 999.99 | 0.028439 | 0.031874 | 0.03211 | 999.99 | 16 | 0 | 0.032483 | 0.84267 | 999.99 | 0.83219 | 0.83808 | 0.84779 | 999.99 | 8 | 0.83219 | 0.83
3 | Feb | 0.02734 | 999.99 | 0.03158 | 0.026967 | 0.027792 | 999.99 | 8 | 0 | 0.035192 | 0.83307 | 999.99 | 0.83042 | 0.83919 | 0.8475 | 999.99 | 8 | 0.83042 | 0.83
4 | Feb | 0.028969 | 0.025652 | 0.028989 | 0.027399 | 999.99 | 999.99 | 8 | 0 | 0.029107 | 0.83154 | 0.83866 | 0.82506 | 0.82812 | 999.99 | 999.99 | 8 | 0.82506 | 0.83
5 | Feb | 0.028282 | 999.99 | 0.028439 | 0.028459 | 999.99 | 999.99 | 12 | 0 | 0.030245 | 0.82836 | 999.99 | 0.81605 | 0.83448 | 999.99 | 999.99 | 8 | 0.81605 | 0.82
6 | Feb | 0.029617 | 999.99 | 0.030618 | 0.035172 | 0.048324 | 999.99 | 16 | 0 | 0.049698 | 0.83472 | 999.99 | 0.81352 | 0.82383 | 0.83478 | 999.99 | 16 | 0.82 | 0.82
7 | Feb | 0.03898 | 999.99 | 0.046164 | 0.02842 | 0.025142 | 999.99 | 8 | 0 | 0.048461 | 0.81853 | 999.99 | 0.80775 | 0.81558 | 0.8233 | 999.99 | 8 | 0.80775 | 0.81
8 | Feb | 0.025102 | 999.99 | 999.99 | 999.99 | 999.99 | 0.024514 | 0 | 0 | 0.02893 | 0.81258 | 999.99 | 999.99 | 999.99 | 999.99 | 0.78466 | 20 | 0.78466 | 0.78
9 | Feb | 999.99 | 0.028047 | 999.99 | 999.99 | 999.99 | 0.027929 | 4 | 0 | 0.028361 | 999.99 | 0.78496 | 999.99 | 999.99 | 999.99 | 0.78514 | 4 | 0.78496 | 0.78
10 | Feb | 999.99 | 0.028479 | 999.99 | 0.026221 | 0.026732 | 0.033739 | 20 | 0 | 0.033739 | 999.99 | 0.78025 | 999.99 | 0.78573 | 0.78855 | 0.79544 | 4 | 0.78025 | 0.78
11 | Feb | 999.99 | 0.040001 | 0.04271 | 0.028852 | 0.029068 | 999.99 | 8 | 0 | 0.04271 | 999.99 | 0.77589 | 0.7703 | 0.7826 | 0.79044 | 999.99 | 8 | 0.7703 | 0.77
12 | Feb | 999.99 | 0.028361 | 0.028302 | 0.027693 | 0.025966 | 999.99 | 4 | 0 | 0.029028 | 999.99 | 0.77448 | 0.78196 | 0.79209 | 0.78443 | 999.99 | 4 | 0.77448 | 0.77
13 | Feb | 0.028734 | 0.026437 | 0.029166 | 0.027301 | 999.99 | 0.025338 | 8 | 0 | 0.031737 | 0.77289 | 0.78154 | 0.77972 | 0.79562 | 999.99 | 0.78484 | 4 | 0.77 | 0.77
14 | Feb | 999.99 | 0.032562 | 0.027399 | 0.045399 | 0.028341 | 999.99 | 12 | 0 | 0.045831 | 999.99 | 0.79597 | 0.79756 | 0.80734 | 0.81187 | 999.99 | 8 | 0.79597 | 0.8
15 | Feb | 0.027006 | 999.99 | 0.026692 | 0.024887 | 999.99 | 0.027674 | 0 | 0 | 0.028714 | 0.82636 | 999.99 | 0.82388 | 0.83066 | 999.99 | 0.82065 | 20 | 0.82065 | 0.82
16 | Feb | 999.99 | 0.02787 | 0.024219 | 0.024887 | 999.99 | 0.02789 | 4 | 0 | 0.02842 | 999.99 | 0.83018 | 0.8336 | 0.84538 | 999.99 | 0.83272 | 4 | 0.83018 | 0.83
17 | Feb | 0.024749 | 0.026241 | 0.028439 | 0.028086 | 999.99 | 999.99 | 12 | 0 | 0.028538 | 0.83931 | 0.83937 | 0.82171 | 0.81858 | 999.99 | 999.99 | 12 | 0.81858 | 0.82
18 | Feb | 0.027792 | 999.99 | 0.027281 | 0.027635 | 999.99 | 0.027674 | 12 | 0 | 0.031325 | 0.80551 | 999.99 | 0.78785 | 0.78726 | 999.99 | 0.76476 | 20 | 0.76476 | 0.76
19 | Feb | 0.026967 | 0.029166 | 999.99 | 0.027046 | 999.99 | 0.02842 | 0 | 0 | 0.030854 | 0.78484 | 0.79697 | 999.99 | 0.79373 | 999.99 | 0.76217 | 20 | 0.76217 | 0.76
20 | Feb | 999.99 | 999.99 | 0.027517 | 999.99 | 999.99 | 0.028439 | 20 | 0 | 0.030226 | 999.99 | 999.99 | 0.7551 | 999.99 | 999.99 | 0.7455 | 20 | 0.7455 | 0.75
21 | Feb | 999.99 | 999.99 | 0.028596 | 0.027419 | 999.99 | 999.99 | 12 | 0 | 0.031325 | 999.99 | 999.99 | 0.75186 | 0.77059 | 999.99 | 999.99 | 8 | 0.75186 | 0.75
22 | Feb | 0.028302 | 999.99 | 999.99 | 0.029931 | 999.99 | 0.029126 | 0 | 0 | 0.030756 | 0.76282 | 999.99 | 999.99 | 0.75793 | 999.99 | 0.76352 | 12 | 0.75793 | 0.76
23 | Feb | 999.99 | 999.99 | 0.026791 | 0.029735 | 999.99 | 0.029382 | 8 | 0 | 0.030265 | 999.99 | 999.99 | 0.76835 | 0.77518 | 999.99 | 0.76405 | 20 | 0.76405 | 0.76
24 | Feb | 999.99 | 0.030402 | 0.025946 | 0.027242 | 999.99 | 0.029774 | 12 | 0 | 0.030873 | 999.99 | 0.75381 | 0.77571 | 0.78761 | 999.99 | 0.77495 | 4 | 0.75381 | 0.75
25 | Feb | 0.026751 | 0.03001 | 999.99 | 999.99 | 999.99 | 999.99 | 4 | 0 | 0.030029 | 0.79338 | 0.78655 | 999.99 | 999.99 | 999.99 | 999.99 | 4 | 0.78655 | 0.79
26 | Feb | 0.030972 | 999.99 | 0.031443 | 999.99 | 0.027909 | 0.031325 | 20 | 0 | 0.03209 | 0.77554 | 999.99 | 0.76617 | 999.99 | 0.77489 | 0.77937 | 8 | 0.76617 | 0.77
27 | Feb | 999.99 | 0.029087 | 999.99 | 999.99 | 0.028518 | 0.030815 | 20 | 0 | 0.033347 | 999.99 | 0.77742 | 999.99 | 999.99 | 0.76759 | 0.77094 | 20 | 0.76759 | 0.77
28 | Feb | 999.99 | 0.034897 | 0.032974 | 999.99 | 0.034034 | 0.039805 | 20 | 0 | 0.039864 | 999.99 | 0.7693 | 0.78973 | 999.99 | 0.7743 | 0.79085 | 16 | 0.7693 | 0.77