## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Apr_21
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.02 | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02
2 | 0.02 | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02
3 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
4 | 0.02 | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02
5 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
6 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
7 | 0.02 | 0.02 | 0.022492 | 0.02 | 0.022354 | 0.02 | 0.02
8 | 0.02 | 0.024533 | 0.02 | OFF | 0.02 | 0.02 | 0.02
9 | 0.02 | 0.03 | 0.03 | 0.02 | OFF | 0.02 | 0.03
10 | 0.023611 | OFF | 0.02 | OFF | 0.02365 | 0.02 | 0.02
11 | OFF | 0.024847 | OFF | 0.023571 | OFF | 0.02 | 0.02
12 | 0.023355 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
13 | 0.02 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02
14 | OFF | OFF | 0.023768 | 0.02 | OFF | 0.023198 | 0.02
15 | OFF | OFF | 0.02 | 0.02 | OFF | 0.031835 | 0.02
16 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
17 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
18 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
19 | 0.02 | OFF | 0.02 | 0.034976 | OFF | 0.02 | 0.02
20 | OFF | 0.02 | OFF | 0.02 | OFF | 0.02 | 0.02
21 | 0.02 | 0.02 | OFF | OFF | 0.02 | 0.02 | 0.02
22 | 0.02 | 0.02 | OFF | 0.02 | OFF | 0.02 | 0.02
23 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
24 | 0.02 | 0.02 | 0.02 | OFF | OFF | OFF | 0.02
25 | OFF | 0.02 | 0.02 | 0.02 | OFF | OFF | 0.02
26 | 0.02 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02
27 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
28 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
29 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
30 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Ricardo R. Saavedra
[5 empty] | SIGNATURE: Ricardo R. Saavedra |  |  | DATE: 05/07/2021
[5 empty] | PHONE #: (541) 336-2610 |  |  | CERT #:T-09181
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Apr_21 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 16:00 | 0.81 | 111 | 89.91 | 8.7 | 7.26 | 22.5256 | YES | 831
2 / 8:00 | 0.82 | 111 | 91.02 | 9.2 | 7.05 | 20.2735 | YES | 835
3 / 8:00 | 0.83 | 111 | 92.13 | 9.4 | 6.89 | 18.9518 | YES | 867
4 / 8:00 | 0.82 | 111 | 91.02 | 9.1 | 7.28 | 22.1181 | YES | 854
5 / 20:00 | 0.76 | 111 | 84.36 | 9.2 | 7.33 | 22.2113 | YES | 1055
6 / 8:00 | 0.73 | 111 | 81.03 | 9.7 | 7.4 | 21.9514 | YES | 1011
7 / 4:00 | 0.74 | 111 | 82.14 | 9.1 | 7.53 | 23.9414 | YES | 1031
8 / 8:00 | 0.75 | 111 | 83.25 | 9.2 | 7.76 | 25.8399 | YES | 963
9 / 8:00 | 0.75 | 111 | 83.25 | 9.2 | 7.7 | 25.2927 | YES | 896
10 / 8:00 | 0.81 | 111 | 89.91 | 9.5 | 7.68 | 24.7844 | YES | 893
11 / 4:00 | 0.81 | 111 | 89.91 | 9.4 | 7.6 | 24.2509 | YES | 877
12 / 8:00 | 0.82 | 111 | 91.02 | 9.6 | 7.6 | 23.9574 | YES | 833
13 / 12:00 | 0.82 | 111 | 91.02 | 9.6 | 7.48 | 22.9614 | YES | 854
14 / 12:00 | 0.82 | 111 | 91.02 | 9.7 | 7.5 | 22.9714 | YES | 818
15 / 20:00 | 0.83 | 111 | 92.13 | 9.8 | 7.45 | 22.4464 | YES | 837
16 / 12:00 | 0.83 | 111 | 92.13 | 10.6 | 7.42 | 21.0708 | YES | 874
17 / 16:00 | 0.81 | 111 | 89.91 | 11.1 | 7.37 | 19.9948 | YES | 881
18 / 20:00 | 0.8 | 111 | 88.8 | 11.6 | 7.36 | 19.2658 | YES | 875
19 / 20:00 | 0.72 | 111 | 79.92 | 12.2 | 7.37 | 18.431 | YES | 1005
20 / 20:00 | 0.67 | 111 | 74.37 | 12.3 | 7.37 | 18.2114 | YES | 978
21 / 16:00 | 0.66 | 111 | 73.26 | 12.6 | 7.37 | 17.6358 | YES | 999
22 / 20:00 | 0.65 | 111 | 72.15 | 12.8 | 7.33 | 17.1279 | YES | 1034
23 / 4:00 | 0.66 | 111 | 73.26 | 13 | 7.37 | 17.1727 | YES | 1006
24 / 4:00 | 0.7 | 111 | 77.7 | 12.7 | 7.36 | 17.5337 | YES | 1116
25 / 8:00 | 0.71 | 111 | 78.81 | 12.6 | 7.32 | 17.4116 | YES | 899
26 / 24:00 | 0.75 | 111 | 83.25 | 12.5 | 7.28 | 17.3493 | YES | 857
27 / 8:00 | 0.78 | 111 | 86.58 | 12.2 | 7.31 | 18.1746 | YES | 806
28 / 20:00 | 0.8 | 111 | 88.8 | 11.6 | 7.31 | 18.9355 | YES | 832
29 / 12:00 | 0.78 | 111 | 86.58 | 12.1 | 7.32 | 18.3553 | YES | 829
30 / 8:00 | 0.77 | 111 | 85.47 | 12.5 | 7.34 | 17.7785 | YES | 870
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Apr | 0.051562 | 999.99 | 0.055076 | 999.99 | 0.054154 | 0.054742 | 16 | 0 | 0.057176 | 0.82553 | 999.99 | 0.81264 | 999.99 | 0.80781 | 0.82471 | 16 | 0.80781 | 0.81
2 | Apr | 0.056941 | 999.99 | 0.05433 | 999.99 | 0.052878 | 0.05804 | 20 | 0 | 0.058236 | 0.8286 | 999.99 | 0.81752 | 999.99 | 0.82188 | 0.8313 | 8 | 0.81752 | 0.82
3 | Apr | 0.060239 | 999.99 | 0.055253 | 0.055645 | 0.05855 | 0.056372 | 16 | 0 | 0.062535 | 0.83643 | 999.99 | 0.83331 | 0.84361 | 0.84008 | 0.84208 | 8 | 0.83331 | 0.83
4 | Apr | 0.055155 | 999.99 | 0.057491 | 999.99 | 0.052858 | 0.05382 | 8 | 0 | 0.057608 | 0.8293 | 999.99 | 0.81711 | 999.99 | 0.82029 | 0.82365 | 8 | 0.81711 | 0.82
5 | Apr | 0.053722 | 999.99 | 0.055096 | 0.057903 | 0.069445 | 0.054369 | 16 | 0 | 0.074725 | 0.83172 | 999.99 | 0.81417 | 0.7998 | 0.77442 | 0.75646 | 20 | 0.75646 | 0.76
6 | Apr | 999.99 | 0.054919 | 0.051582 | 0.026398 | 0.022197 | 0.023728 | 4 | 0 | 0.055567 | 999.99 | 0.73279 | 0.72796 | 0.73349 | 0.74062 | 0.75251 | 8 | 0.72796 | 0.73
7 | Apr | 0.025907 | 0.025534 | 0.022492 | 0.026045 | 0.022354 | 0.023238 | 4 | 0 | 0.026889 | 0.74315 | 0.74215 | 0.75628 | 0.74733 | 0.74715 | 0.75033 | 4 | 0.74215 | 0.74
8 | Apr | 0.025613 | 0.024533 | 0.026064 | 999.99 | 0.025554 | 0.030559 | 20 | 0 | 0.030795 | 0.7597 | 0.75027 | 0.74951 | 999.99 | 0.75905 | 0.75993 | 8 | 0.74951 | 0.75
9 | Apr | 0.033661 | 0.041277 | 0.033936 | 0.027006 | 999.99 | 0.024671 | 4 | 0 | 0.043358 | 0.76276 | 0.77224 | 0.74939 | 0.75469 | 999.99 | 0.79803 | 8 | 0.74939 | 0.75
10 | Apr | 0.023611 | 999.99 | 0.025672 | 999.99 | 0.02365 | 0.02577 | 8 | 0 | 0.028027 | 0.81075 | 999.99 | 0.81134 | 999.99 | 0.82253 | 0.81976 | 8 | 0.81134 | 0.81
11 | Apr | 999.99 | 0.024847 | 999.99 | 0.023571 | 999.99 | 0.026064 | 12 | 0 | 0.027046 | 999.99 | 0.80557 | 999.99 | 0.81075 | 999.99 | 0.81181 | 4 | 0.80557 | 0.81
12 | Apr | 0.023355 | 999.99 | 0.025397 | 0.027379 | 999.99 | 0.026653 | 12 | 0 | 0.027497 | 0.83001 | 999.99 | 0.82218 | 0.82471 | 999.99 | 0.81682 | 8 | 0.81682 | 0.82
13 | Apr | 0.026535 | 999.99 | 999.99 | 0.02681 | 0.026889 | 0.026555 | 12 | 0 | 0.026948 | 0.8207 | 999.99 | 999.99 | 0.81723 | 0.82689 | 0.83113 | 12 | 0.81723 | 0.82
14 | Apr | 999.99 | 999.99 | 0.023768 | 0.026732 | 999.99 | 0.023198 | 8 | 0 | 0.027654 | 999.99 | 999.99 | 0.82706 | 0.82412 | 999.99 | 0.83778 | 12 | 0.82412 | 0.82
15 | Apr | 999.99 | 999.99 | 0.026123 | 0.028852 | 999.99 | 0.031835 | 20 | 0 | 0.034367 | 999.99 | 999.99 | 0.8283 | 0.83278 | 999.99 | 0.82783 | 20 | 0.82783 | 0.83
16 | Apr | 999.99 | 999.99 | 0.032601 | 0.033955 | 0.033916 | 0.032247 | 20 | 0 | 0.035035 | 999.99 | 999.99 | 0.82512 | 0.82824 | 0.83631 | 0.83931 | 12 | 0.82512 | 0.83
17 | Apr | 0.033837 | 999.99 | 0.031109 | 0.03425 | 0.034524 | 0.033798 | 20 | 0 | 0.037135 | 0.82088 | 999.99 | 0.82229 | 0.82206 | 0.81434 | 0.82565 | 16 | 0.81434 | 0.81
18 | Apr | 999.99 | 999.99 | 0.03158 | 0.034662 | 999.99 | 0.031109 | 12 | 0 | 0.037861 | 999.99 | 999.99 | 0.81016 | 0.80946 | 999.99 | 0.7968 | 20 | 0.7968 | 0.8
19 | Apr | 0.031207 | 999.99 | 0.035113 | 0.034976 | 999.99 | 0.03211 | 12 | 0 | 0.035879 | 0.80469 | 999.99 | 0.78443 | 0.76718 | 999.99 | 0.71942 | 20 | 0.71942 | 0.72
20 | Apr | 999.99 | 0.035898 | 999.99 | 0.034348 | 999.99 | 0.034407 | 4 | 0 | 0.037096 | 999.99 | 0.68968 | 999.99 | 0.68397 | 999.99 | 0.67166 | 20 | 0.67166 | 0.67
21 | Apr | 0.032404 | 0.035447 | 999.99 | 999.99 | 0.033504 | 0.031639 | 4 | 0 | 0.036154 | 0.68656 | 0.67195 | 999.99 | 999.99 | 0.65623 | 0.67655 | 16 | 0.65623 | 0.66
22 | Apr | 0.034524 | 0.033504 | 999.99 | 0.032071 | 999.99 | 0.032267 | 12 | 0 | 0.035938 | 0.67148 | 0.68014 | 999.99 | 0.68067 | 999.99 | 0.65093 | 20 | 0.65093 | 0.65
23 | Apr | 999.99 | 0.034603 | 0.033543 | 0.034485 | 0.034446 | 999.99 | 8 | 0 | 0.0358 | 999.99 | 0.67213 | 0.65947 | 0.71453 | 0.72077 | 999.99 | 4 | 0.66 | 0.66
24 | Apr | 0.033582 | 0.033955 | 0.0316 | 999.99 | 999.99 | 999.99 | 4 | 0 | 0.037057 | 0.70081 | 0.6994 | 0.72855 | 999.99 | 999.99 | 999.99 | 4 | 0.6994 | 0.7
25 | Apr | 999.99 | 0.03474 | 0.033072 | 0.035153 | 999.99 | 999.99 | 4 | 0 | 0.035467 | 999.99 | 0.7087 | 0.70093 | 0.73061 | 999.99 | 999.99 | 8 | 0.70093 | 0.7
26 | Apr | 0.03476 | 0.033896 | 999.99 | 0.032856 | 0.035997 | 999.99 | 4 | 0 | 0.036232 | 0.75428 | 0.76729 | 999.99 | 0.79815 | 0.80162 | 999.99 | 24 | 0.75428 | 0.75
27 | Apr | 999.99 | 0.036016 | 0.035781 | 0.033936 | 999.99 | 0.036723 | 12 | 0 | 0.036821 | 999.99 | 0.77978 | 0.77907 | 0.79344 | 999.99 | 0.78137 | 8 | 0.77907 | 0.78
28 | Apr | 0.03315 | 999.99 | 0.033818 | 0.032483 | 999.99 | 0.033268 | 0 | 0 | 0.036291 | 0.80221 | 999.99 | 0.80215 | 0.80622 | 999.99 | 0.79738 | 20 | 0.79738 | 0.8
29 | Apr | 999.99 | 999.99 | 0.03582 | 0.035192 | 0.035702 | 999.99 | 12 | 0 | 0.035957 | 999.99 | 999.99 | 0.77636 | 0.78296 | 0.7942 | 999.99 | 12 | 0.78 | 0.78
30 | Apr | 999.99 | 999.99 | 0.034112 | 0.034564 | 0.034564 | 0.03423 | 16 | 0 | 0.04059 | 999.99 | 999.99 | 0.77059 | 0.78172 | 0.79173 | 0.77995 | 8 | 0.77059 | 0.77