## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Jul_21
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
2 | OFF | 0.02 | 0.02 | OFF | 0.02 | OFF | 0.02
3 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
4 | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
5 | 0.02 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02
6 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
7 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
8 | OFF | 0.02 | 0.02 | OFF | 0.03 | 0.03 | 0.03
9 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
10 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
11 | 0.02 | 0.02 | 0.02 | 0.03 | OFF | 0.03 | 0.03
12 | 0.03 | OFF | 0.02 | 0.03 | OFF | 0.02 | 0.03
13 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
14 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
15 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.03 | 0.03
16 | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02 | 0.02
17 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
18 | 0.02 | 0.02 | 0.02 | 0.05 | 0.02 | 0.02 | 0.05
19 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
20 | 0.02 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02
21 | OFF | 0.02 | 0.08 | 0.02 | 0.02 | OFF | 0.08
22 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
23 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
24 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
25 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
26 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
27 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | OFF | 0.03
28 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
29 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
30 | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02 | 0.02
31 | 0.02 | OFF | 0.02 | OFF | 0.03 | OFF | 0.03
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Ricardo R. Saavedra
[5 empty] | SIGNATURE: Ricardo R.Saavedra |  |  | DATE:08/07/2021
[5 empty] | PHONE #: (541) 336-2610 |  |  | CERT #: T-09181
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Jul_21 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 4:00 | 0.64 | 111 | 71.04 | 20.2 | 7.36 | 10.5379 | YES | 1015
2 / 4:00 | 0.68 | 111 | 75.48 | 19.2 | 7.34 | 11.2406 | YES | 1019
3 / 20:00 | 0.73 | 111 | 81.03 | 18.9 | 7.39 | 11.7536 | YES | 1036
4 / 4:00 | 0.76 | 111 | 84.36 | 18.9 | 7.35 | 11.6193 | YES | 991
5 / 12:00 | 0.8 | 111 | 88.8 | 19.1 | 7.42 | 11.8219 | YES | 1005
6 / 20:00 | 0.79 | 111 | 87.69 | 19.5 | 7.43 | 11.5379 | YES | 974
7 / 20:00 | 0.78 | 111 | 86.58 | 19.7 | 7.39 | 11.2016 | YES | 985
8 / 16:00 | 0.79 | 111 | 87.69 | 19.5 | 7.4 | 11.4092 | YES | 1000
9 / 24:00 | 0.8 | 111 | 88.8 | 18.9 | 7.44 | 12.0717 | YES | 1028
10 / 20:00 | 0.79 | 111 | 87.69 | 18.8 | 7.42 | 12.0489 | YES | 1017
11 / 20:00 | 0.78 | 111 | 86.58 | 18.9 | 7.48 | 12.2252 | YES | 993
12 / 20:00 | 0.77 | 111 | 85.47 | 19.2 | 7.45 | 11.8342 | YES | 967
13 / 20:00 | 0.76 | 111 | 84.36 | 19.4 | 7.38 | 11.3614 | YES | 973
14 / 20:00 | 0.73 | 111 | 81.03 | 19.5 | 7.47 | 11.6312 | YES | 1001
15 / 4:00 | 0.74 | 111 | 82.14 | 19.5 | 7.43 | 11.4718 | YES | 1074
16 / 16:00 | 0.75 | 111 | 83.25 | 19.4 | 7.49 | 11.8246 | YES | 1041
17 / 8:00 | 0.77 | 111 | 85.47 | 19.5 | 7.48 | 11.7285 | YES | 1003
18 / 8:00 | 0.81 | 111 | 89.91 | 19.3 | 7.44 | 11.765 | YES | 991
19 / 8:00 | 0.81 | 111 | 89.91 | 19.3 | 7.44 | 11.765 | YES | 970
20 / 12:00 | 0.79 | 111 | 87.69 | 19.8 | 7.52 | 11.6941 | YES | 984
21 / 4:00 | 0.82 | 111 | 91.02 | 19.6 | 7.49 | 11.7608 | YES | 1041
22 / 8:00 | 0.83 | 111 | 92.13 | 19.6 | 7.47 | 11.6867 | YES | 1018
23 / 12:00 | 0.85 | 111 | 94.35 | 19.1 | 7.57 | 12.5743 | YES | 993
24 / 12:00 | 0.87 | 111 | 96.57 | 18.9 | 7.48 | 12.352 | YES | 1030
25 / 20:00 | 0.85 | 111 | 94.35 | 19.4 | 7.58 | 12.3696 | YES | 980
26 / 20:00 | 0.87 | 111 | 96.57 | 19.1 | 7.46 | 12.0966 | YES | 991
27 / 4:00 | 0.87 | 111 | 96.57 | 20.2 | 7.43 | 11.1083 | YES | 1066
28 / 20:00 | 0.85 | 111 | 94.35 | 20.6 | 7.4 | 10.6673 | YES | 1054
29 / 8:00 | 0.85 | 111 | 94.35 | 20.6 | 7.33 | 10.3909 | YES | 1023
30 / 16:00 | 0.85 | 111 | 94.35 | 20.8 | 7.41 | 10.5638 | YES | 988
31 / 16:00 | 0.83 | 111 | 92.13 | 20.9 | 7.41 | 10.4685 | YES | 999
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Jul | 0.034093 | 0.037214 | 0.03741 | 0.040021 | 999.99 | 0.034544 | 8 | 0 | 0.041041 | 0.67331 | 0.6421 | 0.67001 | 0.69262 | 999.99 | 0.67867 | 4 | 0.6421 | 0.64
2 | Jul | 999.99 | 0.031246 | 0.032326 | 999.99 | 0.035525 | 999.99 | 16 | 0 | 0.038038 | 999.99 | 0.69056 | 0.71041 | 999.99 | 0.71094 | 999.99 | 4 | 0.69056 | 0.69
3 | Jul | 0.030167 | 999.99 | 0.031992 | 0.034387 | 999.99 | 0.03527 | 8 | 0 | 0.038548 | 0.72637 | 999.99 | 0.73226 | 0.74986 | 999.99 | 0.73108 | 20 | 0.73108 | 0.73
4 | Jul | 0.032758 | 0.031129 | 0.030363 | 0.032856 | 999.99 | 0.033347 | 12 | 0 | 0.038038 | 0.76606 | 0.76111 | 0.77218 | 0.7932 | 999.99 | 0.78667 | 4 | 0.76111 | 0.76
5 | Jul | 0.0305 | 0.031737 | 999.99 | 0.035761 | 0.030481 | 0.032149 | 12 | 0 | 0.036252 | 0.82123 | 0.80645 | 999.99 | 0.80969 | 0.81694 | 0.82459 | 12 | 0.8 | 0.8
6 | Jul | 0.034721 | 999.99 | 0.031187 | 0.030854 | 999.99 | 0.03105 | 0 | 0 | 0.034721 | 0.8157 | 999.99 | 0.79774 | 0.82076 | 999.99 | 0.79273 | 20 | 0.79273 | 0.79
7 | Jul | 0.033582 | 999.99 | 0.031207 | 0.033366 | 999.99 | 0.035153 | 20 | 0 | 0.035447 | 0.80781 | 999.99 | 0.7965 | 0.7995 | 999.99 | 0.78119 | 20 | 0.78119 | 0.78
8 | Jul | 999.99 | 0.031462 | 0.032797 | 999.99 | 0.038921 | 0.036016 | 20 | 0 | 0.039667 | 999.99 | 0.79621 | 0.80775 | 999.99 | 0.7796 | 0.80009 | 16 | 0.7796 | 0.78
9 | Jul | 0.036566 | 999.99 | 0.034544 | 0.038509 | 999.99 | 0.033779 | 12 | 0 | 0.038666 | 0.78696 | 999.99 | 0.8157 | 0.82159 | 999.99 | 0.80504 | 24 | 0.80504 | 0.81
10 | Jul | 999.99 | 0.03529 | 0.03686 | 0.037371 | 999.99 | 0.032679 | 12 | 0 | 0.038666 | 999.99 | 0.81252 | 0.81046 | 0.826 | 999.99 | 0.7965 | 20 | 0.7965 | 0.8
11 | Jul | 0.03633 | 0.036742 | 0.037292 | 0.039687 | 999.99 | 0.039746 | 12 | 0 | 0.042278 | 0.80857 | 0.78325 | 0.79862 | 0.79974 | 999.99 | 0.7763 | 20 | 0.7763 | 0.78
12 | Jul | 0.03688 | 999.99 | 0.038647 | 0.036291 | 999.99 | 0.034701 | 8 | 0 | 0.038647 | 0.80233 | 999.99 | 0.78131 | 0.79209 | 999.99 | 0.76924 | 20 | 0.76924 | 0.77
13 | Jul | 0.037508 | 999.99 | 0.03849 | 0.03635 | 999.99 | 0.038764 | 12 | 0 | 0.038921 | 0.79415 | 999.99 | 0.78849 | 0.79002 | 999.99 | 0.75563 | 20 | 0.75563 | 0.76
14 | Jul | 999.99 | 0.035035 | 0.039726 | 0.038804 | 999.99 | 0.042023 | 20 | 0 | 0.042042 | 999.99 | 0.76506 | 0.7607 | 0.7693 | 999.99 | 0.73367 | 20 | 0.73367 | 0.73
15 | Jul | 999.99 | 0.03688 | 0.036507 | 0.041964 | 0.041277 | 0.042651 | 12 | 0 | 0.042867 | 999.99 | 0.74391 | 0.75775 | 0.75805 | 0.765 | 0.76553 | 4 | 0.74391 | 0.74
16 | Jul | 0.041414 | 0.037449 | 0.036016 | 999.99 | 0.039353 | 0.041159 | 0 | 0 | 0.041944 | 0.76682 | 0.75186 | 0.77495 | 999.99 | 0.75033 | 0.77159 | 16 | 0.75033 | 0.75
17 | Jul | 0.040374 | 999.99 | 0.036782 | 0.036428 | 999.99 | 0.036605 | 0 | 0 | 0.040943 | 0.76641 | 999.99 | 0.7776 | 0.79597 | 999.99 | 0.78366 | 8 | 0.7776 | 0.78
18 | Jul | 0.039294 | 0.039785 | 0.038117 | 0.059728 | 0.039314 | 0.039569 | 12 | 0 | 0.059728 | 0.81234 | 0.80198 | 0.79668 | 0.81287 | 0.82577 | 0.83978 | 8 | 0.79668 | 0.8
19 | Jul | 999.99 | 0.038666 | 0.038529 | 0.041807 | 0.041355 | 999.99 | 12 | 0 | 0.042121 | 999.99 | 0.84361 | 0.82318 | 0.827 | 0.82123 | 999.99 | 8 | 0.81 | 0.81
20 | Jul | 0.038234 | 999.99 | 999.99 | 0.043358 | 0.043142 | 0.041944 | 12 | 0 | 0.043416 | 0.81635 | 999.99 | 999.99 | 0.78732 | 0.7942 | 0.81882 | 12 | 0.78732 | 0.79
21 | Jul | 999.99 | 0.03849 | 0.088701 | 0.045242 | 0.042396 | 999.99 | 8 | 0 | 0.09035 | 999.99 | 0.81699 | 0.82683 | 0.8455 | 0.86181 | 999.99 | 4 | 0.81699 | 0.82
22 | Jul | 0.041826 | 999.99 | 0.046694 | 0.043416 | 0.044457 | 0.046066 | 16 | 0 | 0.051288 | 0.86369 | 999.99 | 0.82971 | 0.86575 | 0.87682 | 0.88259 | 8 | 0.82971 | 0.83
23 | Jul | 0.045595 | 999.99 | 0.046773 | 0.044182 | 0.044555 | 0.046125 | 16 | 0 | 0.047833 | 0.86746 | 999.99 | 0.85539 | 0.85774 | 0.88083 | 0.8833 | 12 | 0.85 | 0.85
24 | Jul | 999.99 | 0.047715 | 0.049816 | 0.048893 | 0.04797 | 0.050836 | 12 | 0 | 0.052308 | 999.99 | 0.88848 | 0.8614 | 0.87559 | 0.88689 | 0.89196 | 12 | 0.87 | 0.87
25 | Jul | 0.049403 | 999.99 | 0.051033 | 0.048402 | 999.99 | 0.05276 | 20 | 0 | 0.052956 | 0.88471 | 999.99 | 0.86446 | 0.88283 | 999.99 | 0.84679 | 20 | 0.84679 | 0.85
26 | Jul | 0.051778 | 999.99 | 0.052799 | 0.050797 | 999.99 | 0.054742 | 20 | 0 | 0.054742 | 0.87005 | 999.99 | 0.88177 | 0.90898 | 999.99 | 0.86658 | 20 | 0.86658 | 0.87
27 | Jul | 0.054193 | 0.072821 | 0.053839 | 0.057667 | 0.059826 | 999.99 | 4 | 0 | 0.072821 | 0.90562 | 0.87317 | 0.88407 | 0.88466 | 0.87865 | 999.99 | 4 | 0.87317 | 0.87
28 | Jul | 0.057196 | 999.99 | 0.058688 | 0.062182 | 999.99 | 0.063203 | 20 | 0 | 0.063281 | 0.87211 | 999.99 | 0.84756 | 0.84938 | 999.99 | 0.84614 | 20 | 0.84614 | 0.85
29 | Jul | 0.061573 | 999.99 | 0.066834 | 0.063948 | 999.99 | 0.063693 | 12 | 0 | 0.067501 | 0.87005 | 999.99 | 0.85333 | 0.87329 | 999.99 | 0.85933 | 8 | 0.85333 | 0.85
30 | Jul | 0.06336 | 0.064891 | 0.066755 | 999.99 | 1.0013 | 0.078886 | 16 | 0 | 1.0013 | 0.89213 | 0.881 | 0.89337 | 999.99 | 0.85415 | 0.86463 | 16 | 0.85415 | 0.85
31 | Jul | 0.076472 | 999.99 | 0.080084 | 999.99 | 0.059355 | 999.99 | 8 | 0 | 0.082204 | 0.88324 | 999.99 | 0.86434 | 999.99 | 0.82094 | 999.99 | 16 | 0.82094 | 0.82