## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Sep_21
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.02 | OFF | 0.02 | OFF | OFF | OFF | 0.02
2 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
3 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
4 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | OFF | 0.03
5 | 0.03 | OFF | 0.03 | OFF | 0.02 | OFF | 0.03
6 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
7 | 0.02 | 0.02 | 0.02 | OFF | OFF | OFF | 0.02
8 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
9 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
10 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
11 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
12 | OFF | 0.02 | 0.02 | 0.03 | OFF | 0.02 | 0.03
13 | 0.02 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
14 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
15 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
16 | OFF | 0.02 | 0.02 | 0.03 | OFF | 0.03 | 0.03
17 | OFF | 0.03 | OFF | 0.02 | OFF | OFF | 0.03
18 | OFF | 0.03 | 0.02 | OFF | 0.02 | OFF | 0.03
19 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
20 | 0.03 | OFF | 0.03 | 0.03 | 0.03 | 0.02 | 0.03
21 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
22 | OFF | 0.02 | 0.02 | 0.03 | 0.061416 | OFF | 0.061416
23 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
24 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
25 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
26 | OFF | 0.02 | 0.07 | 0.02 | 0.02 | OFF | 0.07
27 | 0.02 | 0.02 | 0.2 | OFF | 0.021 | OFF | 0.02
28 | 0.038215 | OFF | 0.035722 | 0.038882 | 0.039981 | 0.041964 | 0.041983
29 | OFF | 0.04 | 0.02 | OFF | OFF | 0.03 | 0.04
30 | OFF | 0.02 | 0.08 | 0.03 | 0.02 | OFF | 0.08
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Ricardo R Saavedra
[5 empty] | SIGNATURE: Ricardo R Saavedra |  |  | DATE:10/05/2021
[5 empty] | PHONE #: ( 541 ) 336-2610 |  |  | CERT #:T-09181
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Sep_21 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 8:00 | 0.78 | 111 | 86.58 | 18.1 | 7.3 | 12.0623 | YES | 988
2 / 24:00 | 0.77 | 111 | 85.47 | 17.9 | 7.14 | 11.5032 | YES | 994
3 / 4:00 | 0.75 | 111 | 83.25 | 17.7 | 7.25 | 12.12 | YES | 994
4 / 4:00 | 0.77 | 111 | 85.47 | 17.4 | 7.38 | 13.0103 | YES | 1013
5 / 16:00 | 0.77 | 111 | 85.47 | 17.5 | 7.34 | 12.7322 | YES | 1031
6 / 20:00 | 0.76 | 111 | 84.36 | 17.7 | 7.27 | 12.2248 | YES | 1022
7 / 4:00 | 0.77 | 111 | 85.47 | 18.1 | 7.43 | 12.6469 | YES | 1025
8 / 24:00 | 0.76 | 111 | 84.36 | 18.3 | 7.4 | 12.3254 | YES | 985
9 / 20:00 | 0.75 | 111 | 83.25 | 18.6 | 7.39 | 12.0207 | YES | 983
10 / 20:00 | 0.74 | 111 | 82.14 | 18.9 | 7.45 | 12.0337 | YES | 1017
11 / 8:00 | 0.74 | 111 | 82.14 | 18.7 | 7.42 | 12.0608 | YES | 972
12 / 4:00 | 0.71 | 111 | 78.81 | 18.2 | 7.44 | 12.5229 | YES | 1035
13 / 12:00 | 0.71 | 111 | 78.81 | 18.2 | 7.43 | 12.4763 | YES | 1006
14 / 24:00 | 0.71 | 111 | 78.81 | 17.8 | 7.38 | 12.5791 | YES | 1045
15 / 20:00 | 0.77 | 111 | 85.47 | 17.5 | 7.4 | 13.0199 | YES | 1061
16 / 20:00 | 0.77 | 111 | 85.47 | 17.3 | 7.42 | 13.2942 | YES | 981
17 / 4:00 | 0.77 | 111 | 85.47 | 17.5 | 7.4 | 13.0199 | YES | 1008
18 / 4:00 | 0.77 | 111 | 85.47 | 16.8 | 7.34 | 13.3439 | YES | 990
19 / 8:00 | 0.77 | 111 | 85.47 | 16.5 | 7.38 | 13.8187 | YES | 842
20 / 20:00 | 0.81 | 111 | 89.91 | 16.1 | 7.4 | 14.3647 | YES | 890
21 / 20:00 | 0.72 | 111 | 79.92 | 15.8 | 7.32 | 14.0813 | YES | 875
22 / 4:00 | 0.73 | 111 | 81.03 | 15.9 | 7.33 | 14.0555 | YES | 824
23 / 24:00 | 0.75 | 111 | 83.25 | 15.8 | 7.32 | 14.1296 | YES | 832
24 / 24:00 | 0.8 | 111 | 88.8 | 15.9 | 7.39 | 14.4875 | YES | 813
25 / 20:00 | 0.84 | 111 | 93.24 | 16.1 | 7.36 | 14.2014 | YES | 831
26 / 4:00 | 0.86 | 111 | 95.46 | 16.3 | 7.47 | 14.6303 | YES | 884
27 / 24:00 | 0.86 | 111 | 95.46 | 16.1 | 7.47 | 14.827 | YES | 898
28 / 8:00 | 0.83 | 111 | 92.13 | 16 | 7.42 | 14.602 | YES | 888
29 / 16:00 | 0.78 | 111 | 86.58 | 15.8 | 7.25 | 13.8141 | YES | 888
30 / 8:00 | 0.77 | 111 | 85.47 | 14.4 | 7.26 | 15.208 | YES | 834
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Sep | 0.20316 | 999.99 | 0.20614 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.20661 | 0.77147 | 999.99 | 0.77901 | 999.99 | 999.99 | 999.99 | 8 | 0.77901 | 0.78
2 | Sep | 0.20759 | 999.99 | 0.20622 | 0.20653 | 999.99 | 0.20526 | 8 | 0 | 0.20893 | 0.77725 | 999.99 | 0.81081 | 0.81611 | 999.99 | 0.77789 | 24 | 0.77 | 0.77
3 | Sep | 999.99 | 0.2065 | 0.20657 | 0.20891 | 0.20669 | 999.99 | 8 | 0 | 0.21034 | 999.99 | 0.76282 | 0.76305 | 0.79203 | 0.79097 | 999.99 | 4 | 0.76282 | 0.76
4 | Sep | 0.21074 | 0.21052 | 0.20791 | 0.2103 | 0.20995 | 999.99 | 8 | 0 | 0.21113 | 0.78737 | 0.77866 | 0.79591 | 0.79473 | 0.81211 | 999.99 | 4 | 0.77866 | 0.78
5 | Sep | 0.20828 | 999.99 | 0.20852 | 999.99 | 0.21223 | 999.99 | 16 | 0 | 0.21223 | 0.78284 | 999.99 | 0.78849 | 999.99 | 0.76729 | 999.99 | 16 | 0.76729 | 0.77
6 | Sep | 0.20964 | 999.99 | 0.21266 | 0.21219 | 999.99 | 0.21327 | 20 | 0 | 0.21333 | 0.76423 | 999.99 | 0.76653 | 0.77895 | 999.99 | 0.75864 | 20 | 0.75864 | 0.76
7 | Sep | 0.21044 | 0.21413 | 0.21431 | 999.99 | 999.99 | 999.99 | 4 | 0 | 0.21488 | 0.78166 | 0.76659 | 0.77942 | 999.99 | 999.99 | 999.99 | 4 | 0.76659 | 0.77
8 | Sep | 0.21433 | 999.99 | 0.21234 | 0.21496 | 0.21466 | 0.2157 | 20 | 0 | 0.21607 | 0.74627 | 999.99 | 0.76482 | 0.77577 | 0.77577 | 0.78449 | 24 | 0.76 | 0.76
9 | Sep | 999.99 | 0.21266 | 0.21337 | 0.21615 | 999.99 | 0.21662 | 20 | 0 | 0.21662 | 999.99 | 0.78408 | 0.77371 | 0.77613 | 999.99 | 0.7521 | 20 | 0.7521 | 0.75
10 | Sep | 999.99 | 0.21527 | 0.21655 | 0.21392 | 999.99 | 0.21344 | 20 | 0 | 0.21766 | 999.99 | 0.74592 | 0.74403 | 0.77772 | 999.99 | 0.74592 | 20 | 0.74403 | 0.74
11 | Sep | 999.99 | 999.99 | 0.21708 | 0.21657 | 0.2136 | 0.21456 | 8 | 0 | 0.21843 | 999.99 | 999.99 | 0.73326 | 0.7534 | 0.75039 | 0.74892 | 8 | 0.73326 | 0.73
12 | Sep | 999.99 | 0.21454 | 0.21863 | 0.21827 | 999.99 | 0.21729 | 8 | 0 | 0.21863 | 999.99 | 0.71859 | 0.7183 | 0.72619 | 999.99 | 0.71329 | 4 | 0.71329 | 0.71
13 | Sep | 0.21935 | 999.99 | 999.99 | 0.21476 | 0.21731 | 999.99 | 16 | 0 | 0.21835 | 0.73867 | 999.99 | 999.99 | 0.71482 | 0.72089 | 999.99 | 12 | 0.71482 | 0.71
14 | Sep | 0.21627 | 999.99 | 0.21733 | 0.21778 | 999.99 | 999.99 | 8 | 0 | 0.21976 | 0.7236 | 999.99 | 0.75716 | 0.78066 | 999.99 | 999.99 | 24 | 0.71 | 0.71
15 | Sep | 999.99 | 0.21798 | 0.21664 | 0.21967 | 999.99 | 0.21965 | 4 | 0 | 0.22031 | 999.99 | 0.77725 | 0.77595 | 0.78861 | 999.99 | 0.76335 | 20 | 0.76335 | 0.76
16 | Sep | 999.99 | 0.21808 | 0.216 | 0.21535 | 999.99 | 0.21715 | 4 | 0 | 0.21973 | 999.99 | 0.77071 | 0.80015 | 0.80245 | 999.99 | 0.77713 | 20 | 0.77071 | 0.77
17 | Sep | 999.99 | 0.21802 | 0.21621 | 0.21715 | 999.99 | 999.99 | 4 | 0 | 0.21953 | 999.99 | 0.77489 | 0.7766 | 0.80557 | 999.99 | 999.99 | 4 | 0.77489 | 0.77
18 | Sep | 999.99 | 0.21531 | 0.217 | 999.99 | 0.21605 | 999.99 | 16 | 0 | 0.21918 | 999.99 | 0.77306 | 0.79144 | 999.99 | 0.78602 | 999.99 | 4 | 0.77306 | 0.77
19 | Sep | 999.99 | 999.99 | 0.21743 | 0.21859 | 0.21568 | 999.99 | 12 | 0 | 0.21912 | 999.99 | 999.99 | 0.78013 | 0.81252 | 0.84143 | 999.99 | 8 | 0.78013 | 0.78
20 | Sep | 0.21562 | 999.99 | 0.21782 | 0.21466 | 0.043102 | 0.036762 | 0 | 0 | 0.21904 | 0.83289 | 999.99 | 0.84073 | 0.84685 | 0.82871 | 0.82294 | 20 | 0.82294 | 0.82
21 | Sep | 999.99 | 0.036782 | 0.033013 | 0.036919 | 999.99 | 0.035898 | 4 | 0 | 0.038784 | 999.99 | 0.7647 | 0.78826 | 0.77719 | 999.99 | 0.72242 | 20 | 0.72242 | 0.72
22 | Sep | 999.99 | 0.03209 | 0.037528 | 0.041964 | 0.061416 | 999.99 | 16 | 0 | 0.061416 | 999.99 | 0.7259 | 0.76252 | 0.78007 | 0.78048 | 999.99 | 4 | 0.7259 | 0.73
23 | Sep | 0.044967 | 0.031992 | 0.031855 | 0.030736 | 0.03156 | 999.99 | 0 | 0 | 0.045124 | 0.7458 | 0.78573 | 0.77783 | 0.81323 | 0.82718 | 999.99 | 24 | 0.7458 | 0.75
24 | Sep | 0.031541 | 0.039451 | 0.030618 | 0.031835 | 0.032228 | 999.99 | 4 | 0 | 0.040354 | 0.80133 | 0.80215 | 0.821 | 0.84526 | 0.86422 | 999.99 | 24 | 0.80215 | 0.8
25 | Sep | 0.032522 | 999.99 | 0.034603 | 0.034623 | 999.99 | 0.03476 | 20 | 0 | 0.035172 | 0.84279 | 999.99 | 0.8588 | 0.86622 | 999.99 | 0.84826 | 20 | 0.84826 | 0.85
26 | Sep | 999.99 | 0.033798 | 0.075726 | 0.035918 | 0.036585 | 999.99 | 8 | 0 | 0.076531 | 999.99 | 0.84891 | 0.89037 | 0.89855 | 0.88501 | 999.99 | 4 | 0.84891 | 0.85
27 | Sep | 0.044398 | 0.036527 | 0.035153 | 999.99 | 0.03319 | 999.99 | 0 | 0 | 0.044398 | 0.86717 | 0.87123 | 0.89043 | 999.99 | 0.8972 | 999.99 | 24 | 0.86 | 0.86
28 | Sep | 0.038215 | 999.99 | 0.035722 | 0.038882 | 0.039981 | 0.041964 | 20 | 0 | 0.041983 | 0.85374 | 999.99 | 0.82724 | 0.83554 | 0.85668 | 0.84762 | 8 | 0.82724 | 0.83
29 | Sep | 999.99 | 0.045144 | 0.041846 | 999.99 | 0.18131 | 0.044241 | 16 | 0 | 0.18131 | 999.99 | 0.80545 | 0.82235 | 999.99 | 0.77513 | 0.78938 | 16 | 0.77513 | 0.78
30 | Sep | 999.99 | 0.044025 | 0.089722 | 0.043593 | 0.042455 | 999.99 | 8 | 0 | 0.08978 | 999.99 | 0.77359 | 0.77153 | 0.80392 | 0.81317 | 999.99 | 8 | 0.77153 | 0.77