## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Apr_22
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | 0.03 | OFF | 0.03 | 0.03 | 0.03 | 0.03
2 | OFF | 0.03 | OFF | 0.03 | 0.03 | OFF | 0.03
3 | OFF | 0.03 | OFF | 0.03 | 0.03 | OFF | 0.03
4 | 0.03 | 0.03 | OFF | 0.03 | OFF | OFF | 0.03
5 | 0.03 | OFF | 0.03 | 0.03 | OFF | OFF | 0.03
6 | 0.03 | OFF | 0.03 | 0.03 | 0.04 | OFF | 0.04
7 | 0.04 | OFF | 0.04 | 0.04 | OFF | OFF | 0.04
8 | 0.03 | OFF | 0.03 | 0.03 | OFF | OFF | 0.03
9 | 0.03 | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
10 | 0.03 | 0.03 | 0.07 | OFF | OFF | 0.03 | 0.07
11 | 0.03 | 0.03 | OFF | 0.03 | OFF | OFF | 0.03
12 | OFF | 0.03 | 0.03 | OFF | OFF | 0.030442 | 0.03
13 | 0.031894 | 0.03 | OFF | 0.05 | 0.03 | OFF | 0.050208
14 | 0.03 | OFF | 0.03 | 0.034858 | 0.03 | OFF | 0.03
15 | 0.03 | OFF | 0.032385 | 0.02 | OFF | 0.03 | 0.03
16 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
17 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
18 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
19 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
20 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
21 | 0.02 | OFF | 0.02 | 0.02 | 0.03 | 0.03 | 0.03
22 | OFF | 0.03 | 0.02 | OFF | 0.03 | 0.03 | 0.03
23 | OFF | 0.03 | OFF | 0.03 | 0.03 | OFF | 0.03
24 | OFF | 0.03 | OFF | 0.03 | 0.03 | 0.03 | 0.03
25 | 0.03 | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
26 | 0.03 | OFF | 0.03 | 0.03 | OFF | 0.03 | 0.03
27 | 0.03 | OFF | 0.03 | OFF | 0.03 | 0.03 | 0.03
28 | 0.03 | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
29 | 0.03 | OFF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
30 | OFF | 0.03 | 0.03 | OFF | 0.03 | OFF | 0.03
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Zachary J Dues
[5 empty] | SIGNATURE: Zachary J Dues |  |  | DATE:05/02/2022
[5 empty] | PHONE #: ( 541 )336-2610 |  |  | CERT #:T-269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Apr_22 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 12:00 | 0.77 | 111 | 85.47 | 9.1 | 7.3 | 22.1487 | YES | 826
2 / 12:00 | 0.74 | 111 | 82.14 | 9.2 | 7.36 | 22.3964 | YES | 831
3 / 12:00 | 0.75 | 111 | 83.25 | 9.5 | 7.38 | 22.1371 | YES | 767
4 / 24:00 | 0.78 | 111 | 86.58 | 9.5 | 7.33 | 21.8253 | YES | 771
5 / 8:00 | 0.77 | 111 | 85.47 | 9.7 | 7.39 | 21.9735 | YES | 752
6 / 8:00 | 0.77 | 111 | 85.47 | 9.5 | 7.42 | 22.5019 | YES | 833
7 / 8:00 | 0.76 | 111 | 84.36 | 9.7 | 7.48 | 22.6552 | YES | 821
8 / 8:00 | 0.74 | 111 | 82.14 | 10 | 7.64 | 23.4472 | YES | 811
9 / 8:00 | 0.74 | 111 | 82.14 | 9.9 | 7.67 | 23.8556 | YES | 841
10 / 24:00 | 0.73 | 111 | 81.03 | 10 | 7.64 | 23.4205 | YES | 819
11 / 12:00 | 0.75 | 111 | 83.25 | 9.8 | 7.73 | 24.56 | YES | 762
12 / 20:00 | 0.72 | 111 | 79.92 | 9.3 | 7.51 | 23.4052 | YES | 793
13 / 24:00 | 0.74 | 111 | 82.14 | 9.2 | 7.54 | 23.8671 | YES | 808
14 / 8:00 | 0.75 | 111 | 83.25 | 9.4 | 7.69 | 24.8682 | YES | 824
15 / 24:00 | 0.77 | 111 | 85.47 | 9.1 | 7.69 | 25.4301 | YES | 823
16 / 8:00 | 0.79 | 111 | 87.69 | 8.9 | 7.69 | 25.8321 | YES | 833
17 / 24:00 | 0.79 | 111 | 87.69 | 9 | 7.65 | 25.2962 | YES | 789
18 / 24:00 | 0.81 | 111 | 89.91 | 8.8 | 7.59 | 25.152 | YES | 804
19 / 8:00 | 0.8 | 111 | 88.8 | 8.7 | 7.68 | 26.1174 | YES | 763
20 / 8:00 | 0.8 | 111 | 88.8 | 8.7 | 7.6 | 25.3821 | YES | 781
21 / 8:00 | 0.79 | 111 | 87.69 | 8.7 | 7.55 | 24.9055 | YES | 827
22 / 4:00 | 0.79 | 111 | 87.69 | 8.7 | 7.5 | 24.4666 | YES | 829
23 / 4:00 | 0.8 | 111 | 88.8 | 8.9 | 7.6 | 25.0449 | YES | 774
24 / 20:00 | 0.82 | 111 | 91.02 | 9.1 | 7.5 | 23.905 | YES | 757
25 / 8:00 | 0.8 | 111 | 88.8 | 9.2 | 7.52 | 23.8611 | YES | 750
26 / 24:00 | 0.79 | 111 | 87.69 | 9.2 | 7.46 | 23.3329 | YES | 847
27 / 16:00 | 0.79 | 111 | 87.69 | 9.4 | 7.46 | 23.0255 | YES | 850
28 / 20:00 | 0.8 | 111 | 88.8 | 9.1 | 7.41 | 23.103 | YES | 749
29 / 8:00 | 0.78 | 111 | 86.58 | 9.4 | 7.39 | 22.4384 | YES | 780
30 / 4:00 | 0.8 | 111 | 88.8 | 9.3 | 7.34 | 22.2433 | YES | 807
31 |  | 111 |  |  |  |  | NO
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Apr | 999.99 | 0.040865 | 999.99 | 0.046714 | 0.039824 | 999.99 | 16 | 0 | 0.048324 | 999.99 | 0.78684 | 999.99 | 0.769 | 0.78278 | 999.99 | 12 | 0.769 | 0.77
2 | Apr | 999.99 | 0.039648 | 999.99 | 0.044771 | 0.041611 | 999.99 | 4 | 0 | 0.046557 | 999.99 | 0.74639 | 999.99 | 0.73685 | 0.75681 | 999.99 | 12 | 0.73685 | 0.74
3 | Apr | 999.99 | 0.044849 | 999.99 | 0.042769 | 0.042965 | 999.99 | 16 | 0 | 0.046125 | 999.99 | 0.76488 | 999.99 | 0.74945 | 0.77683 | 999.99 | 12 | 0.74945 | 0.75
4 | Apr | 0.042985 | 0.041061 | 999.99 | 0.044064 | 999.99 | 0.043436 | 0 | 0 | 0.048952 | 0.77978 | 0.78508 | 999.99 | 0.78902 | 999.99 | 0.77495 | 24 | 0.77495 | 0.77
5 | Apr | 999.99 | 999.99 | 0.046753 | 0.042651 | 999.99 | 0.039844 | 8 | 0 | 0.057039 | 999.99 | 999.99 | 0.77654 | 0.79367 | 999.99 | 0.76606 | 8 | 0.76606 | 0.77
6 | Apr | 999.99 | 999.99 | 0.044849 | 0.040786 | 0.046616 | 999.99 | 16 | 0 | 0.049973 | 999.99 | 999.99 | 0.77012 | 0.77577 | 0.78555 | 999.99 | 8 | 0.77012 | 0.77
7 | Apr | 0.046243 | 999.99 | 0.048383 | 0.04799 | 999.99 | 0.049541 | 20 | 0 | 0.050463 | 0.76111 | 999.99 | 0.75781 | 0.77112 | 999.99 | 0.75228 | 8 | 0.75228 | 0.75
8 | Apr | 999.99 | 999.99 | 0.045399 | 0.045634 | 999.99 | 0.045222 | 12 | 0 | 0.050031 | 999.99 | 999.99 | 0.74521 | 0.76882 | 999.99 | 0.74839 | 8 | 0.74521 | 0.75
9 | Apr | 999.99 | 999.99 | 0.049384 | 0.045831 | 999.99 | 999.99 | 8 | 0 | 0.049639 | 999.99 | 999.99 | 0.74144 | 0.76099 | 999.99 | 999.99 | 8 | 0.74144 | 0.74
10 | Apr | 0.051778 | 0.050071 | 0.061613 | 999.99 | 0.052799 | 0.053251 | 8 | 0 | 0.065146 | 0.74209 | 0.75658 | 0.76023 | 999.99 | 0.74344 | 0.75634 | 24 | 0.73 | 0.73
11 | Apr | 0.050522 | 999.99 | 0.080515 | 0.055017 | 999.99 | 999.99 | 8 | 0 | 0.091174 | 0.75504 | 999.99 | 0.73302 | 0.74333 | 999.99 | 999.99 | 12 | 0.75 | 0.75
12 | Apr | 0.060788 | 0.054291 | 0.051975 | 999.99 | 999.99 | 0.030442 | 0 | 0 | 0.06279 | 0.72307 | 0.72566 | 0.74804 | 999.99 | 999.99 | 0.72036 | 20 | 0.72036 | 0.72
13 | Apr | 0.031894 | 999.99 | 0.050208 | 0.039942 | 999.99 | 999.99 | 8 | 0 | 0.050208 | 0.74127 | 999.99 | 0.74103 | 0.77195 | 999.99 | 999.99 | 24 | 0.74103 | 0.74
14 | Apr | 999.99 | 999.99 | 0.035192 | 0.034858 | 999.99 | 999.99 | 8 | 0 | 0.037528 | 999.99 | 999.99 | 0.75663 | 0.77654 | 999.99 | 999.99 | 8 | 0.75663 | 0.76
15 | Apr | 999.99 | 999.99 | 0.032385 | 0.043829 | 999.99 | 0.045654 | 20 | 0 | 0.051994 | 999.99 | 999.99 | 0.77607 | 0.79515 | 999.99 | 0.78007 | 24 | 0.77607 | 0.78
16 | Apr | 999.99 | 999.99 | 0.040649 | 0.036566 | 999.99 | 0.046694 | 20 | 0 | 0.050581 | 999.99 | 999.99 | 0.78514 | 0.79415 | 999.99 | 0.79055 | 8 | 0.78514 | 0.79
17 | Apr | 999.99 | 999.99 | 0.045458 | 0.04426 | 0.053192 | 999.99 | 16 | 0 | 0.055861 | 999.99 | 999.99 | 0.79685 | 0.81811 | 0.82235 | 999.99 | 24 | 0.79685 | 0.8
18 | Apr | 0.043848 | 999.99 | 0.061711 | 0.055626 | 999.99 | 0.05698 | 8 | 0 | 0.078023 | 0.81853 | 999.99 | 0.81864 | 0.82394 | 999.99 | 0.80339 | 24 | 0.80339 | 0.8
19 | Apr | 999.99 | 999.99 | 0.069896 | 0.048049 | 999.99 | 0.077709 | 20 | 0 | 0.079377 | 999.99 | 999.99 | 0.80846 | 0.81788 | 999.99 | 0.7995 | 8 | 0.7995 | 0.8
20 | Apr | 999.99 | 999.99 | 0.050169 | 0.043318 | 999.99 | 0.17081 | 20 | 0 | 0.1712 | 999.99 | 999.99 | 0.79491 | 0.80869 | 999.99 | 0.79091 | 8 | 0.8 | 0.8
21 | Apr | 999.99 | 999.99 | 999.99 | 0.035879 | 0.039 | 0.033582 | 16 | 0 | 0.039 | 999.99 | 999.99 | 999.99 | 0.80021 | 0.81376 | 0.81005 | 8 | 0.80021 | 0.8
22 | Apr | 999.99 | 0.037704 | 0.035172 | 999.99 | 0.036232 | 0.04271 | 20 | 0 | 0.046106 | 999.99 | 0.79126 | 0.79974 | 999.99 | 0.80133 | 0.80333 | 4 | 0.79126 | 0.79
23 | Apr | 999.99 | 0.03847 | 999.99 | 0.044732 | 0.051739 | 999.99 | 16 | 0 | 0.052348 | 999.99 | 0.79509 | 999.99 | 0.81752 | 0.79568 | 999.99 | 4 | 0.79509 | 0.8
24 | Apr | 999.99 | 0.039039 | 999.99 | 0.043475 | 0.043299 | 0.043475 | 20 | 0 | 0.1026 | 999.99 | 0.81876 | 999.99 | 0.82665 | 0.83018 | 0.81617 | 20 | 0.81617 | 0.82
25 | Apr | 0.040099 | 999.99 | 0.037685 | 0.046793 | 0.041571 | 999.99 | 8 | 0 | 0.05435 | 0.81599 | 999.99 | 0.80392 | 0.81417 | 0.80934 | 999.99 | 8 | 0.80392 | 0.8
26 | Apr | 0.040119 | 999.99 | 0.043299 | 0.045693 | 999.99 | 0.05064 | 20 | 0 | 0.054311 | 0.80215 | 999.99 | 0.80233 | 0.81529 | 999.99 | 0.81122 | 24 | 0.79 | 0.79
27 | Apr | 0.046322 | 999.99 | 0.042513 | 999.99 | 0.04006 | 0.04483 | 20 | 0 | 0.051543 | 0.81252 | 999.99 | 0.80098 | 999.99 | 0.80162 | 0.80257 | 16 | 0.79 | 0.79
28 | Apr | 0.042592 | 999.99 | 0.043809 | 0.044673 | 0.05859 | 999.99 | 16 | 0 | 0.05859 | 0.80981 | 999.99 | 0.7978 | 0.81317 | 0.80834 | 999.99 | 20 | 0.7978 | 0.8
29 | Apr | 0.053898 | 999.99 | 0.049462 | 0.047126 | 0.048775 | 0.047244 | 8 | 0 | 0.059336 | 0.79097 | 999.99 | 0.77778 | 0.79521 | 0.79491 | 0.8038 | 8 | 0.77778 | 0.78
30 | Apr | 999.99 | 0.039353 | 0.046439 | 999.99 | 0.09512 | 999.99 | 16 | 0 | 0.11226 | 999.99 | 0.7955 | 0.79903 | 999.99 | 0.80722 | 999.99 | 4 | 0.7955 | 0.8