## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | May_22
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | 0.03 | 0.03 | 0.14 | 0.03 | 0.03 | 0.14
2 | OFF | 0.03 | 0.06 | 0.13 | 0.08 | OFF | 0.13
3 | OFF | OFF | 0.04 | 0.04 | 0.03 | 0.03 | 0.04
4 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
5 | 0.03 | OFF | 0.03 | OFF | 0.03 | 0.03 | 0.03
6 | 0.03 | OFF | 0.03 | OFF | 0.03 | 0.03 | 0.03
7 | 0.03 | OFF | OFF | 0.03 | 0.04 | 0.03 | 0.04
8 | 0.03 | 0.03 | OFF | 0.03 | OFF | OFF | 0.03
9 | 0.03 | OFF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
10 | OFF | 0.02 | OFF | 0.03 | OFF | 0.03 | 0.03
11 | 0.03 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
12 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
13 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
14 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
15 | OFF | 0.11 | OFF | 0.04 | 0.02 | OFF | 0.11
16 | 0.02 | OFF | 0.02 | 0.03 | 0.02 | 0.02 | 0.03
17 | OFF | 0.02 | OFF | OFF | 0.03 | 0.02 | 0.03
18 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
19 | OFF | OFF | 0.02 | OFF | 0.06 | 0.02 | 0.06
20 | OFF | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02
21 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
22 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
23 | OFF | OFF | 0.02 | 0.020902 | OFF | OFF | 0.02
24 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
25 | 0.02 | 0.024199 | 0.02 | 0.02 | 0.02 | OFF | 0.02
26 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
27 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
28 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
29 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
30 | OFF | 0.02 | OFF | 0.02 | OFF | 0.02 | 0.02
31 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Zachary J Dues
[5 empty] | SIGNATURE: Zachary J Dues |  |  | DATE:06/01/2022
[5 empty] | PHONE #: (541)-336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | May_22 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 4:00 | 0.81 | 111 | 89.91 | 9.4 | 7.29 | 21.7366 | YES | 843
2 / 4:00 | 0.82 | 111 | 91.02 | 9.3 | 7.39 | 22.6899 | YES | 815
3 / 12:00 | 0.82 | 111 | 91.02 | 10 | 7.39 | 21.6652 | YES | 785
4 / 20:00 | 0.8 | 111 | 88.8 | 9 | 7.31 | 22.4502 | YES | 845
5 / 8:00 | 0.77 | 111 | 85.47 | 10 | 7.18 | 20.0197 | YES | 833
6 / 8:00 | 0.75 | 111 | 83.25 | 10 | 7.2 | 20.1144 | YES | 825
7 / 12:00 | 0.73 | 111 | 81.03 | 10 | 7.23 | 20.2802 | YES | 759
8 / 12:00 | 0.73 | 111 | 81.03 | 10 | 7.27 | 20.565 | YES | 765
9 / 8:00 | 0.71 | 111 | 78.81 | 10 | 7.25 | 20.3764 | YES | 791
10 / 4:00 | 0.74 | 111 | 82.14 | 10 | 7.38 | 21.3955 | YES | 850
11 / 20:00 | 0.65 | 111 | 72.15 | 10 | 7.64 | 23.2086 | YES | 897
12 / 24:00 | 0.71 | 111 | 78.81 | 10.8 | 7.64 | 22.162 | YES | 1056
13 / 4:00 | 0.9 | 111 | 99.9 | 10.7 | 7.59 | 22.3958 | YES | 1053
14 / 8:00 | 0.86 | 111 | 95.46 | 10.6 | 7.61 | 22.6012 | YES | 995
15 / 12:00 | 0.85 | 111 | 94.35 | 1.8 | 7.45 | 38.6612 | YES | 1021
16 / 8:00 | 0.85 | 111 | 94.35 | 11 | 7.4 | 20.4285 | YES | 1025
17 / 20:00 | 0.87 | 111 | 96.57 | 11 | 7.4 | 20.4743 | YES | 1035
18 / 16:00 | 0.84 | 111 | 93.24 | 11.4 | 7.5 | 20.5838 | YES | 1080
19 / 8:00 | 0.82 | 111 | 91.02 | 11.3 | 7.4 | 19.9648 | YES | 848
20 / 4:00 | 0.85 | 111 | 94.35 | 11.2 | 7.29 | 19.4073 | YES | 832
21 / 20:00 | 0.85 | 111 | 94.35 | 10.8 | 7.37 | 20.4822 | YES | 852
22 / 20:00 | 0.81 | 111 | 89.91 | 11.5 | 7.33 | 19.2123 | YES | 837
23 / 12:00 | 0.79 | 111 | 87.69 | 12.1 | 7.37 | 18.6949 | YES | 894
24 / 16:00 | 0.77 | 111 | 85.47 | 12.5 | 7.38 | 18.043 | YES | 900
25 / 4:00 | 0.77 | 111 | 85.47 | 12.6 | 7.67 | 19.9467 | YES | 893
26 / 8:00 | 0.76 | 111 | 84.36 | 12.9 | 7.45 | 18.0091 | YES | 868
27 / 8:00 | 0.77 | 111 | 85.47 | 13 | 7.31 | 17.0073 | YES | 858
28 / 24:00 | 0.77 | 111 | 85.47 | 13.1 | 7.54 | 18.3924 | YES | 833
29 / 16:00 | 0.78 | 111 | 86.58 | 12.9 | 7.52 | 18.5224 | YES | 823
30 / 20:00 | 0.77 | 111 | 85.47 | 12.6 | 7.47 | 18.5288 | YES | 834
31 / 16:00 | 0.76 | 111 | 84.36 | 12.5 | 7.44 | 18.4261 | YES | 916
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | May | 999.99 | 0.047597 | 0.046655 | 0.15887 | 0.05327 | 0.041316 | 12 | 0 | 0.15986 | 999.99 | 0.81205 | 0.83437 | 0.83784 | 0.83254 | 0.84014 | 4 | 0.81205 | 0.81
2 | May | 999.99 | 0.045301 | 0.073606 | 0.14672 | 0.084382 | 999.99 | 12 | 0 | 0.14937 | 999.99 | 0.81717 | 0.83372 | 0.88201 | 0.87759 | 999.99 | 4 | 0.81717 | 0.82
3 | May | 999.99 | 999.99 | 0.068934 | 0.059002 | 0.047813 | 0.054193 | 8 | 0 | 0.070701 | 999.99 | 999.99 | 0.82453 | 0.82553 | 0.84078 | 0.83537 | 12 | 0.82453 | 0.82
4 | May | 0.050817 | 0.054311 | 0.0517 | 0.044241 | 0.056823 | 0.053624 | 0 | 0 | 0.059787 | 0.8296 | 0.82294 | 0.81599 | 0.81122 | 0.81682 | 0.80592 | 20 | 0.80592 | 0.81
5 | May | 0.053172 | 999.99 | 0.063301 | 999.99 | 0.057687 | 0.064616 | 20 | 0 | 0.06599 | 0.80051 | 999.99 | 0.76653 | 999.99 | 0.76853 | 0.77165 | 8 | 0.76653 | 0.77
6 | May | 0.049089 | 999.99 | 0.054841 | 999.99 | 0.058531 | 0.046027 | 16 | 0 | 0.058825 | 0.77577 | 999.99 | 0.74768 | 999.99 | 0.73708 | 0.75581 | 8 | 0.73708 | 0.74
7 | May | 0.056529 | 999.99 | 999.99 | 0.0697 | 0.058197 | 0.059336 | 12 | 0 | 0.071192 | 0.75234 | 999.99 | 999.99 | 0.7289 | 0.73738 | 0.75681 | 12 | 0.7289 | 0.73
8 | May | 0.058923 | 0.046459 | 999.99 | 0.093039 | 999.99 | 999.99 | 12 | 0 | 0.10859 | 0.75493 | 0.76276 | 999.99 | 0.73196 | 999.99 | 999.99 | 12 | 0.73196 | 0.73
9 | May | 0.049423 | 999.99 | 0.056921 | 0.052544 | 0.057098 | 0.046596 | 8 | 0 | 0.063733 | 0.72071 | 999.99 | 0.71453 | 0.73926 | 0.74939 | 0.76794 | 8 | 0.71453 | 0.71
10 | May | 999.99 | 0.039864 | 999.99 | 0.050404 | 999.99 | 0.054762 | 20 | 0 | 0.069504 | 999.99 | 0.74144 | 999.99 | 0.75357 | 999.99 | 0.76729 | 4 | 0.74144 | 0.74
11 | May | 0.037783 | 999.99 | 0.049776 | 0.042886 | 0.04165 | 0.041061 | 8 | 0 | 0.051818 | 0.78137 | 999.99 | 0.77036 | 0.78331 | 0.70116 | 0.65882 | 20 | 0.65882 | 0.66
12 | May | 0.041061 | 999.99 | 0.050306 | 0.040217 | 0.044162 | 0.038804 | 8 | 0 | 0.061279 | 0.70104 | 999.99 | 0.75251 | 0.85315 | 0.90244 | 0.90962 | 24 | 0.71 | 0.71
13 | May | 999.99 | 0.045065 | 0.042671 | 0.04642 | 0.046636 | 999.99 | 16 | 0 | 0.054114 | 999.99 | 0.90256 | 0.90839 | 0.92564 | 0.90256 | 999.99 | 4 | 0.90256 | 0.9
14 | May | 0.05062 | 999.99 | 0.045477 | 0.041257 | 999.99 | 0.049423 | 0 | 0 | 0.050817 | 0.88495 | 999.99 | 0.86134 | 0.86116 | 999.99 | 0.85392 | 8 | 0.85392 | 0.85
15 | May | 999.99 | 0.12872 | 999.99 | 0.063399 | 0.10113 | 999.99 | 4 | 0 | 0.12876 | 999.99 | 0.85751 | 999.99 | 0.86428 | 0.86564 | 999.99 | 12 | 0.85751 | 0.86
16 | May | 0.1065 | 999.99 | 0.081732 | 0.073429 | 0.06809 | 0.068777 | 0 | 0 | 0.12227 | 0.85615 | 999.99 | 0.84114 | 0.8684 | 0.87406 | 0.88707 | 8 | 0.84114 | 0.84
17 | May | 999.99 | 0.040178 | 999.99 | 999.99 | 0.094747 | 0.067992 | 16 | 0 | 0.10399 | 999.99 | 0.88507 | 999.99 | 999.99 | 0.88159 | 0.87665 | 20 | 0.87665 | 0.88
18 | May | 999.99 | 0.083303 | 0.1016 | 0.085619 | 0.09777 | 999.99 | 8 | 0 | 0.14215 | 999.99 | 0.85568 | 0.83625 | 0.83236 | 0.83154 | 999.99 | 16 | 0.83154 | 0.83
19 | May | 999.99 | 999.99 | 0.051033 | 999.99 | 0.096945 | 0.054016 | 16 | 0 | 0.10682 | 999.99 | 999.99 | 0.8233 | 999.99 | 0.84355 | 0.85751 | 8 | 0.8233 | 0.82
20 | May | 999.99 | 0.042494 | 999.99 | 0.15821 | 0.033877 | 999.99 | 12 | 0 | 0.16029 | 999.99 | 0.8528 | 999.99 | 0.86693 | 0.876 | 999.99 | 4 | 0.8528 | 0.85
21 | May | 0.052426 | 0.039608 | 0.029912 | 999.99 | 0.045733 | 0.027458 | 0 | 0 | 0.052603 | 0.8591 | 0.86699 | 0.86246 | 999.99 | 0.85027 | 0.85186 | 20 | 0.85027 | 0.85
22 | May | 0.035094 | 999.99 | 0.038607 | 0.027733 | 999.99 | 0.02891 | 8 | 0 | 0.040668 | 0.84332 | 999.99 | 0.81776 | 0.81275 | 999.99 | 0.81058 | 20 | 0.81058 | 0.81
23 | May | 999.99 | 999.99 | 0.038509 | 0.020902 | 999.99 | 999.99 | 8 | 0 | 0.038921 | 999.99 | 999.99 | 0.78955 | 0.78902 | 999.99 | 999.99 | 12 | 0.78902 | 0.79
24 | May | 0.033798 | 999.99 | 0.035997 | 0.035663 | 0.025318 | 999.99 | 8 | 0 | 0.035997 | 0.78361 | 999.99 | 0.76623 | 0.77854 | 0.77766 | 999.99 | 16 | 0.76623 | 0.77
25 | May | 0.032149 | 0.024199 | 0.036546 | 0.029499 | 0.027046 | 999.99 | 8 | 0 | 0.046557 | 0.78366 | 0.77624 | 0.86787 | 0.78584 | 0.7816 | 999.99 | 4 | 0.77624 | 0.78
26 | May | 0.035408 | 999.99 | 0.05009 | 0.043063 | 0.045006 | 0.03637 | 8 | 0 | 0.051661 | 0.76653 | 999.99 | 0.76447 | 0.77477 | 0.78749 | 0.78961 | 8 | 0.76447 | 0.76
27 | May | 999.99 | 0.066461 | 0.03262 | 0.040413 | 0.031443 | 999.99 | 4 | 0 | 0.068463 | 999.99 | 0.78172 | 0.77106 | 0.78525 | 0.78414 | 999.99 | 8 | 0.77106 | 0.77
28 | May | 0.036546 | 999.99 | 0.033837 | 0.032463 | 0.02999 | 999.99 | 12 | 0 | 0.040276 | 0.77006 | 999.99 | 0.7763 | 0.78885 | 0.78431 | 999.99 | 24 | 0.77 | 0.77
29 | May | 0.037901 | 999.99 | 0.063222 | 0.034583 | 0.023257 | 0.029009 | 8 | 0 | 0.064321 | 0.78584 | 999.99 | 0.77277 | 0.78249 | 0.78885 | 0.78272 | 16 | 0.78 | 0.78
30 | May | 999.99 | 0.031698 | 999.99 | 0.025632 | 999.99 | 0.039707 | 20 | 0 | 0.049953 | 999.99 | 0.78567 | 999.99 | 0.78573 | 999.99 | 0.76299 | 20 | 0.76299 | 0.76
31 | May | 0.030481 | 999.99 | 0.031187 | 0.03158 | 0.029951 | 0.032208 | 16 | 0 | 0.038666 | 0.77253 | 999.99 | 0.76405 | 0.76052 | 0.76117 | 0.77312 | 16 | 0.76052 | 0.76