## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Jun_22
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
2 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
3 | OFF | 0.02 | 0.02 | 0.021412 | 0.02 | 0.02 | 0.02
4 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
5 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02 | 0.02
6 | OFF | 0.02 | 0.023414 | 0.02 | 0.02 | OFF | 0.02
7 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
8 | 0.01 | OFF | 0.01 | 0.01 | 0.01 | OFF | 0.01
9 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
10 | OFF | 0.01 | 0.096592 | 0.01 | OFF | 0.01 | 0.01
11 | 0.01 | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
12 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.024219 | 0.02
13 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
14 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
15 | 0.02 | OFF | 0.02 | 0.02 | 0.01 | OFF | 0.02
16 | 0.01 | OFF | 0.01 | 0.01 | OFF | 0.01 | 0.01
17 | OFF | OFF | 0.01 | 0.01 | OFF | 0.01 | 0.01
18 | OFF | OFF | 0.01 | 0.01 | OFF | 0.01 | 0.01
19 | 0.01 | OFF | 0.01 | 0.024042 | 0.02 | 0.02 | 0.02
20 | 0.02 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02
21 | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02
22 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.017761 | 0.02
23 | OFF | 0.02 | 0.02 | 0.018311 | 0.01 | OFF | 0.02
24 | OFF | OFF | 0.01 | 0.01 | 0.01 | OFF | 0.01
25 | 0.01 | OFF | 0.01 | 0.01 | 0.01 | OFF | 0.01
26 | 0.01 | OFF | 0.01 | OFF | 0.01 | 0.01 | 0.01
27 | 0.01 | OFF | 0.01 | 0.01 | 0.02 | OFF | 0.02
28 | 0.02 | 0.02 | 0.02 | 0.024729 | OFF | 0.021 | 0.02
29 | OFF | OFF | 0.02 | 0.018193 | 0.022668 | OFF | 0.02
30 | 0.016328 | OFF | 0.01674 | 0.01992 | OFF | 0.02 | 0.02
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Zachary J. Dues
[5 empty] | SIGNATURE: Zachary J. Dues |  |  | DATE:07-01-2022
[5 empty] | PHONE #: ( 541 )336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Jun_22 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 8:00 | 0.75 | 111 | 83.25 | 12.6 | 7.28 | 17.2343 | YES | 887
2 / 8:00 | 0.76 | 111 | 84.36 | 11.5 | 7.4 | 19.5747 | YES | 842
3 / 4:00 | 0.76 | 111 | 84.36 | 13.6 | 7.63 | 18.3714 | YES | 898
4 / 8:00 | 0.75 | 111 | 83.25 | 13.7 | 7.61 | 18.0949 | YES | 816
5 / 16:00 | 0.74 | 111 | 82.14 | 13.6 | 7.44 | 17.0876 | YES | 835
6 / 16:00 | 0.75 | 111 | 83.25 | 13.3 | 7.48 | 17.7117 | YES | 850
7 / 12:00 | 0.72 | 111 | 79.92 | 13.5 | 7.25 | 15.9979 | YES | 860
8 / 8:00 | 0.74 | 111 | 82.14 | 13.2 | 7.46 | 17.6786 | YES | 851
9 / 4:00 | 0.77 | 111 | 85.47 | 13.2 | 7.33 | 16.9069 | YES | 851
10 / 8:00 | 0.77 | 111 | 85.47 | 13.5 | 7.52 | 17.7781 | YES | 903
11 / 16:00 | 0.76 | 111 | 84.36 | 13.2 | 7.4 | 17.3304 | YES | 844
12 / 8:00 | 0.73 | 111 | 81.03 | 13 | 7.52 | 18.2957 | YES | 853
13 / 8:00 | 0.74 | 111 | 82.14 | 12.8 | 7.45 | 18.0881 | YES | 842
14 / 24:00 | 0.76 | 111 | 84.36 | 12.3 | 7.77 | 21.1334 | YES | 857
15 / 8:00 | 0.78 | 111 | 86.58 | 12.4 | 7.66 | 20.2497 | YES | 867
16 / 20:00 | 0.77 | 111 | 85.47 | 12.4 | 7.64 | 20.0868 | YES | 883
17 / 20:00 | 0.77 | 111 | 85.47 | 12.7 | 7.56 | 19.0275 | YES | 915
18 / 8:00 | 0.77 | 111 | 85.47 | 12.7 | 7.57 | 19.0978 | YES | 872
19 / 8:00 | 0.77 | 111 | 85.47 | 12.7 | 7.62 | 19.453 | YES | 836
20 / 20:00 | 0.78 | 111 | 86.58 | 12.5 | 7.59 | 19.5183 | YES | 837
21 / 20:00 | 0.76 | 111 | 84.36 | 13.6 | 7.65 | 18.5075 | YES | 838
22 / 20:00 | 0.72 | 111 | 79.92 | 13.6 | 7.55 | 17.756 | YES | 849
23 / 4:00 | 0.71 | 111 | 78.81 | 13.8 | 7.43 | 16.7422 | YES | 861
24 / 8:00 | 0.72 | 111 | 79.92 | 14.3 | 7.2 | 14.888 | YES | 871
25 / 8:00 | 0.72 | 111 | 79.92 | 14.5 | 7.36 | 15.5882 | YES | 888
26 / 8:00 | 0.7 | 111 | 77.7 | 15.1 | 7.38 | 15.0534 | YES | 860
27 / 8:00 | 0.74 | 111 | 82.14 | 15.3 | 7.4 | 15.0327 | YES | 829
28 / 20:00 | 0.72 | 111 | 79.92 | 16 | 7.47 | 14.6899 | YES | 846
29 / 8:00 | 0.71 | 111 | 78.81 | 16.1 | 7.51 | 14.7934 | YES | 843
30 / 8:00 | 0.73 | 111 | 81.03 | 16 | 7.35 | 14.0659 | YES | 825
31 |  | 111
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Jun | 0.030972 | 999.99 | 0.030402 | 0.029813 | 999.99 | 999.99 | 0 | 0 | 0.034858 | 0.76229 | 999.99 | 0.75628 | 0.75893 | 999.99 | 999.99 | 8 | 0.75628 | 0.76
2 | Jun | 0.035997 | 999.99 | 0.036114 | 0.038666 | 0.03368 | 0.032542 | 20 | 0 | 0.044241 | 0.77248 | 999.99 | 0.75057 | 0.76847 | 0.78137 | 0.78573 | 8 | 0.75057 | 0.75
3 | Jun | 999.99 | 0.037744 | 0.03633 | 0.021412 | 999.99 | 0.034642 | 20 | 0 | 0.047951 | 999.99 | 0.76741 | 0.77206 | 0.78449 | 999.99 | 0.764 | 4 | 0.764 | 0.76
4 | Jun | 999.99 | 999.99 | 0.042455 | 0.030638 | 0.043318 | 0.041885 | 8 | 0 | 0.048127 | 999.99 | 999.99 | 0.75363 | 0.75828 | 0.76935 | 0.7587 | 8 | 0.75363 | 0.75
5 | Jun | 999.99 | 0.034917 | 0.05592 | 999.99 | 0.040315 | 0.029087 | 8 | 0 | 0.057922 | 999.99 | 0.75493 | 0.76941 | 999.99 | 0.74221 | 0.74568 | 16 | 0.74221 | 0.74
6 | Jun | 999.99 | 0.029087 | 0.023414 | 0.027026 | 0.02736 | 999.99 | 16 | 0 | 0.030088 | 999.99 | 0.7438 | 0.74874 | 0.74162 | 0.74356 | 999.99 | 16 | 0.75 | 0.75
7 | Jun | 0.030245 | 999.99 | 0.040315 | 0.033563 | 0.22554 | 0.075412 | 16 | 0 | 0.23305 | 0.72183 | 999.99 | 0.70829 | 0.71901 | 0.72984 | 0.74668 | 12 | 0.72 | 0.72
8 | Jun | 0.099085 | 999.99 | 0.082027 | 0.26685 | 0.22968 | 999.99 | 12 | 0 | 0.27569 | 0.75675 | 999.99 | 0.73738 | 0.75493 | 0.76411 | 999.99 | 8 | 0.73738 | 0.74
9 | Jun | 0.28427 | 0.26258 | 0.23527 | 0.036487 | 0.039432 | 0.038313 | 4 | 0 | 0.28315 | 0.76099 | 0.77171 | 0.77259 | 0.78402 | 0.78779 | 0.79409 | 4 | 0.77171 | 0.77
10 | Jun | 999.99 | 0.068856 | 0.096592 | 0.075176 | 999.99 | 0.098457 | 20 | 0 | 0.098515 | 999.99 | 0.77318 | 0.76818 | 0.78107 | 999.99 | 0.76865 | 8 | 0.76818 | 0.77
11 | Jun | 0.070465 | 0.029205 | 0.056764 | 0.031168 | 0.028695 | 999.99 | 8 | 0 | 0.074921 | 0.76411 | 0.77077 | 0.76682 | 0.765 | 0.75534 | 999.99 | 16 | 0.75534 | 0.76
12 | Jun | 0.057746 | 999.99 | 0.051562 | 0.057451 | 0.026202 | 0.024219 | 12 | 0 | 0.071211 | 0.73096 | 999.99 | 0.73414 | 0.73897 | 0.75722 | 0.75098 | 8 | 0.73414 | 0.73
13 | Jun | 999.99 | 0.077591 | 0.12327 | 0.072723 | 0.072683 | 0.044751 | 8 | 0 | 0.16013 | 999.99 | 0.73767 | 0.73349 | 0.75575 | 0.76364 | 0.76812 | 8 | 0.73349 | 0.73
14 | Jun | 0.044516 | 999.99 | 0.063556 | 0.050915 | 0.06493 | 999.99 | 8 | 0 | 0.070406 | 0.76111 | 999.99 | 0.75928 | 0.76729 | 0.77895 | 999.99 | 24 | 0.75928 | 0.76
15 | Jun | 0.044908 | 999.99 | 0.044575 | 0.11524 | 0.11889 | 999.99 | 16 | 0 | 0.12138 | 0.78113 | 999.99 | 0.77742 | 0.78684 | 0.7998 | 999.99 | 8 | 0.77742 | 0.78
16 | Jun | 0.084422 | 999.99 | 0.057373 | 0.042769 | 999.99 | 0.091704 | 20 | 0 | 0.092254 | 0.78896 | 999.99 | 0.79391 | 0.78849 | 999.99 | 0.77536 | 20 | 0.77536 | 0.78
17 | Jun | 999.99 | 999.99 | 0.078513 | 0.078631 | 999.99 | 0.044103 | 12 | 0 | 0.10203 | 999.99 | 999.99 | 0.76782 | 0.78249 | 999.99 | 0.76741 | 20 | 0.76741 | 0.77
18 | Jun | 999.99 | 999.99 | 0.039962 | 0.025593 | 999.99 | 0.11438 | 20 | 0 | 0.15246 | 999.99 | 999.99 | 0.75987 | 0.76617 | 999.99 | 0.76294 | 8 | 0.75987 | 0.76
19 | Jun | 0.089859 | 999.99 | 0.02789 | 0.024042 | 0.028871 | 0.026771 | 0 | 0 | 0.10847 | 0.77583 | 999.99 | 0.7786 | 0.78684 | 0.79126 | 0.78313 | 8 | 0.7786 | 0.78
20 | Jun | 0.053918 | 0.052662 | 999.99 | 0.1406 | 0.02469 | 0.026791 | 12 | 0 | 0.16143 | 0.78408 | 0.78808 | 999.99 | 0.7786 | 0.78137 | 0.77495 | 20 | 0.77495 | 0.77
21 | Jun | 999.99 | 0.094864 | 999.99 | 0.11149 | 0.15713 | 0.19544 | 16 | 0 | 0.34439 | 999.99 | 0.76082 | 999.99 | 0.75534 | 0.76924 | 0.76058 | 20 | 0.75534 | 0.76
22 | Jun | 999.99 | 0.25604 | 0.23519 | 0.25412 | 999.99 | 0.017761 | 8 | 0 | 0.30293 | 999.99 | 0.73314 | 0.73903 | 0.74003 | 999.99 | 0.71789 | 20 | 0.71789 | 0.72
23 | Jun | 999.99 | 0.061259 | 0.017467 | 0.018311 | 0.02257 | 999.99 | 4 | 0 | 0.061259 | 999.99 | 0.71259 | 0.7206 | 0.72796 | 0.72554 | 999.99 | 4 | 0.71259 | 0.71
24 | Jun | 999.99 | 999.99 | 0.027988 | 0.02098 | 0.019901 | 999.99 | 16 | 0 | 0.02946 | 999.99 | 999.99 | 0.71724 | 0.73137 | 0.72407 | 999.99 | 8 | 0.71724 | 0.72
25 | Jun | 0.019469 | 999.99 | 0.023866 | 0.021667 | 0.02047 | 999.99 | 12 | 0 | 0.02418 | 0.71076 | 999.99 | 0.70434 | 0.71977 | 0.72383 | 999.99 | 8 | 0.70434 | 0.7
26 | Jun | 0.023728 | 999.99 | 0.027792 | 999.99 | 0.023787 | 0.024572 | 8 | 0 | 0.028027 | 0.7011 | 999.99 | 0.6941 | 999.99 | 0.7054 | 0.72537 | 8 | 0.6941 | 0.69
27 | Jun | 0.024828 | 999.99 | 0.0263 | 0.023591 | 0.024533 | 999.99 | 12 | 0 | 0.02891 | 0.75298 | 999.99 | 0.7332 | 0.75593 | 0.74574 | 999.99 | 8 | 0.7332 | 0.73
28 | Jun | 0.027183 | 0.026025 | 0.028518 | 0.024729 | 999.99 | 0.029342 | 20 | 0 | 0.02946 | 0.72925 | 0.72613 | 0.72972 | 0.73673 | 999.99 | 0.71777 | 20 | 0.71777 | 0.72
29 | Jun | 999.99 | 999.99 | 0.027988 | 0.018193 | 0.022668 | 999.99 | 8 | 0 | 0.028086 | 999.99 | 999.99 | 0.71724 | 0.70911 | 0.73385 | 999.99 | 8 | 0.70911 | 0.71
30 | Jun | 0.016328 | 999.99 | 0.01674 | 0.01992 | 999.99 | 0.029774 | 20 | 0 | 0.031109 | 0.73326 | 999.99 | 0.73067 | 0.7478 | 999.99 | 0.73926 | 8 | 0.73067 | 0.73