## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Aug_22
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
2 | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
3 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
4 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
5 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
6 | OFF | OFF | OFF | OFF | OFF | 0.02 | 0.02
7 | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
8 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
9 | OFF | 0.02 | 0.02 | 0.02 | OFF | OFF | 0.02
10 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
11 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
12 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
13 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
14 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
15 | OFF | 0.02 | OFF | 0.02 | OFF | OFF | 0.02
16 | 0.02 | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02
17 | OFF | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02
18 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
19 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
20 | OFF | 0.02 | 0.02 | OFF | OFF | OFF | 0.02
21 | 0.02 | 0.02 | OFF | OFF | 0.02 | OFF | 0.02
22 | 0.02 | 0.02 | 0.024082 | OFF | 0.022688 | OFF | 0.02
23 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
24 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
25 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
26 | 0.02 | OFF | 0.02 | 0.03 | 0.02 | OFF | 0.03
27 | 0.02 | OFF | 0.02 | 0.03 | 0.02 | OFF | 0.03
28 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
29 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
30 | OFF | OFF | 0.02 | 0.03 | OFF | OFF | 0.03
31 | 0.02 | 0.02 | 0.02 | 0.02 | OFF | OFF | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Zachary J. Dues
[5 empty] | SIGNATURE: Zachary J. Dues |  |  | DATE: 09/07/2022
[5 empty] | PHONE #: ( 541 )336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Aug_22 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 8:00 | 0.72 | 111 | 79.92 | 20.1 | 7.48 | 11.1997 | YES | 814
2 / 20:00 | 0.71 | 111 | 78.81 | 19.9 | 7.41 | 11.0454 | YES | 837
3 / 8:00 | 0.72 | 111 | 79.92 | 19.8 | 7.37 | 10.9674 | YES | 867
4 / 20:00 | 0.74 | 111 | 82.14 | 19.6 | 7.34 | 11.0175 | YES | 901
5 / 8:00 | 0.74 | 111 | 82.14 | 20.5 | 7.28 | 10.1374 | YES | 877
6 / 20:00 | 0.74 | 111 | 82.14 | 19.7 | 7.32 | 10.8618 | YES | 889
7 / 20:00 | 0.75 | 111 | 83.25 | 19.6 | 7.36 | 11.1131 | YES | 796
8 / 8:00 | 0.75 | 111 | 83.25 | 19.8 | 7.36 | 10.9642 | YES | 824
9 / 12:00 | 0.76 | 111 | 84.36 | 19.6 | 7.37 | 11.1676 | YES | 834
10 / 8:00 | 0.74 | 111 | 82.14 | 19.3 | 7.37 | 11.3693 | YES | 830
11 / 8:00 | 0.75 | 111 | 83.25 | 19.1 | 7.28 | 11.1548 | YES | 855
12 / 12:00 | 0.75 | 111 | 83.25 | 19 | 7.21 | 10.9398 | YES | 859
13 / 20:00 | 0.73 | 111 | 81.03 | 18.9 | 7.3 | 11.3649 | YES | 905
14 / 12:00 | 0.74 | 111 | 82.14 | 18.9 | 7.28 | 11.2931 | YES | 823
15 / 12:00 | 0.76 | 111 | 84.36 | 19.2 | 7.4 | 11.6018 | YES | 828
16 / 16:00 | 0.74 | 111 | 82.14 | 19.3 | 7.37 | 11.3693 | YES | 829
17 / 16:00 | 0.74 | 111 | 82.14 | 19.5 | 7.41 | 11.3863 | YES | 837
18 / 8:00 | 0.74 | 111 | 82.14 | 19.9 | 7.13 | 9.9788 | YES | 853
19 / 20:00 | 0.73 | 111 | 81.03 | 20.1 | 7.24 | 10.2481 | YES | 901
20 / 4:00 | 0.72 | 111 | 79.92 | 20.4 | 7.26 | 10.1064 | YES | 855
21/ 24:00 | 0.74 | 111 | 82.14 | 20.1 | 7.2 | 10.107 | YES | 880
22/ 24:00 | 0.74 | 111 | 82.14 | 20.1 | 7.28 | 10.4151 | YES | 826
23 / 20:00 | 0.75 | 111 | 83.25 | 20.1 | 7.28 | 10.4271 | YES | 836
24 / 20:00 | 0.73 | 111 | 81.03 | 20.3 | 7.39 | 10.6958 | YES | 819
25 / 4:00 | 0.72 | 111 | 79.92 | 20.4 | 7.23 | 9.9931 | YES | 890
26/ 24:00 | 0.72 | 111 | 79.92 | 20.6 | 7.19 | 9.7116 | YES | 898
27/ 24:00 | 0.73 | 111 | 81.03 | 20.4 | 7.23 | 10.0047 | YES | 862
28 / 16:00 | 0.75 | 111 | 83.25 | 20.3 | 7.27 | 10.2487 | YES | 832
29 / 20:00 | 0.73 | 111 | 81.03 | 19.9 | 7.37 | 10.9063 | YES | 846
30 / 8:00 | 0.72 | 111 | 79.92 | 19.9 | 7.33 | 10.7317 | YES | 820
31 / 4:00 | 0.71 | 111 | 78.81 | 19.5 | 7.21 | 10.5283 | YES | 871
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Aug | 999.99 | 999.99 | 0.030795 | 0.031776 | 0.027478 | 999.99 | 8 | 0 | 0.034367 | 999.99 | 999.99 | 0.71747 | 0.72389 | 0.73608 | 999.99 | 8 | 0.71747 | 0.72
2 | Aug | 0.031482 | 0.034721 | 0.034308 | 0.033818 | 999.99 | 0.034662 | 12 | 0 | 0.035977 | 0.72572 | 0.7352 | 0.73308 | 0.73343 | 999.99 | 0.70646 | 20 | 0.70646 | 0.71
3 | Aug | 999.99 | 999.99 | 0.034701 | 0.034819 | 0.036154 | 0.036958 | 12 | 0 | 0.03796 | 999.99 | 999.99 | 0.72572 | 0.74333 | 0.75964 | 0.77312 | 8 | 0.72572 | 0.73
4 | Aug | 999.99 | 0.039 | 0.033406 | 0.036939 | 999.99 | 0.034799 | 4 | 0 | 0.040354 | 999.99 | 0.74321 | 0.76694 | 0.77666 | 999.99 | 0.74168 | 20 | 0.74168 | 0.74
5 | Aug | 999.99 | 999.99 | 0.037037 | 0.034151 | 0.029166 | 999.99 | 8 | 0 | 0.037587 | 999.99 | 999.99 | 0.73379 | 0.75575 | 0.76506 | 999.99 | 8 | 0.73379 | 0.73
6 | Aug | 999.99 | 999.99 | 999.99 | 999.99 | 999.99 | 0.034446 | 20 | 0 | 0.039098 | 999.99 | 999.99 | 999.99 | 999.99 | 999.99 | 0.73985 | 20 | 0.73985 | 0.74
7 | Aug | 0.035761 | 0.031423 | 0.64511 | 0.033347 | 999.99 | 0.031737 | 8 | 0 | 0.67689 | 0.7604 | 0.7816 | 0.76871 | 0.76653 | 999.99 | 0.73231 | 20 | 0.73231 | 0.73
8 | Aug | 999.99 | 999.99 | 0.037547 | 0.036841 | 0.033641 | 0.039844 | 16 | 0 | 0.044084 | 999.99 | 999.99 | 0.74798 | 0.768 | 0.7766 | 0.77118 | 8 | 0.74798 | 0.75
9 | Aug | 999.99 | 0.035467 | 0.042788 | 0.035525 | 999.99 | 999.99 | 8 | 0 | 0.042788 | 999.99 | 0.76506 | 0.7501 | 0.77336 | 999.99 | 999.99 | 12 | 0.7501 | 0.75
10 | Aug | 999.99 | 999.99 | 0.038647 | 0.035427 | 999.99 | 999.99 | 8 | 0 | 0.038725 | 999.99 | 999.99 | 0.74174 | 0.77359 | 999.99 | 999.99 | 8 | 0.74174 | 0.74
11 | Aug | 999.99 | 999.99 | 0.033975 | 0.037292 | 0.03529 | 999.99 | 12 | 0 | 0.04006 | 999.99 | 999.99 | 0.75693 | 0.77312 | 0.77483 | 999.99 | 8 | 0.75693 | 0.76
12 | Aug | 999.99 | 0.046322 | 0.039765 | 0.64203 | 0.037371 | 0.032974 | 12 | 0 | 0.64882 | 999.99 | 0.76435 | 0.75923 | 0.74863 | 0.76235 | 0.76953 | 12 | 0.74863 | 0.75
13 | Aug | 999.99 | 999.99 | 0.036448 | 0.035054 | 999.99 | 0.040335 | 20 | 0 | 0.04059 | 999.99 | 999.99 | 0.74303 | 0.75528 | 999.99 | 0.73072 | 20 | 0.73072 | 0.73
14 | Aug | 999.99 | 999.99 | 0.041709 | 0.034466 | 0.036684 | 0.035349 | 8 | 0 | 0.043907 | 999.99 | 999.99 | 0.73579 | 0.74456 | 0.74998 | 0.78184 | 12 | 0.73579 | 0.74
15 | Aug | 999.99 | 0.034976 | 999.99 | 0.035565 | 999.99 | 999.99 | 4 | 0 | 0.035722 | 999.99 | 0.78343 | 999.99 | 0.76894 | 999.99 | 999.99 | 12 | 0.76894 | 0.77
16 | Aug | 0.039942 | 999.99 | 0.038509 | 999.99 | 0.035467 | 0.038666 | 8 | 0 | 0.03898 | 0.73644 | 999.99 | 0.74833 | 999.99 | 0.74462 | 0.76352 | 16 | 0.74462 | 0.74
17 | Aug | 999.99 | 999.99 | 0.037999 | 999.99 | 0.036016 | 0.036939 | 8 | 0 | 0.039844 | 999.99 | 999.99 | 0.73597 | 999.99 | 0.73502 | 0.75846 | 16 | 0.73502 | 0.74
18 | Aug | 999.99 | 999.99 | 0.035427 | 0.039648 | 0.040963 | 0.039216 | 16 | 0 | 0.040963 | 999.99 | 999.99 | 0.73779 | 0.75133 | 0.75039 | 0.75875 | 8 | 0.73779 | 0.74
19 | Aug | 999.99 | 0.042513 | 0.037371 | 0.038921 | 999.99 | 0.03582 | 4 | 0 | 0.043279 | 999.99 | 0.72966 | 0.74721 | 0.75887 | 999.99 | 0.72925 | 20 | 0.72925 | 0.73
20 | Aug | 999.99 | 0.04638 | 0.037272 | 999.99 | 999.99 | 999.99 | 4 | 0 | 0.04638 | 999.99 | 0.71288 | 0.73944 | 999.99 | 999.99 | 999.99 | 4 | 0.71288 | 0.71
21 | Aug | 0.038568 | 0.034112 | 999.99 | 999.99 | 0.025279 | 999.99 | 0 | 0 | 0.038588 | 0.73679 | 0.77348 | 999.99 | 999.99 | 0.74651 | 999.99 | 16 | 0.74651 | 0.75
22 | Aug | 0.034721 | 0.029696 | 0.024082 | 999.99 | 0.022688 | 999.99 | 4 | 0 | 0.036939 | 0.73108 | 0.76111 | 0.7806 | 999.99 | 0.76788 | 999.99 | 4 | 0.76111 | 0.76
23 | Aug | 0.025436 | 999.99 | 0.025907 | 0.031659 | 999.99 | 0.025652 | 8 | 0 | 0.032012 | 0.75711 | 999.99 | 0.75722 | 0.76894 | 999.99 | 0.74462 | 20 | 0.74462 | 0.74
24 | Aug | 999.99 | 0.025358 | 0.027497 | 999.99 | 999.99 | 0.027517 | 8 | 0 | 0.029598 | 999.99 | 0.7259 | 0.76082 | 999.99 | 999.99 | 0.72648 | 20 | 0.7259 | 0.73
25 | Aug | 999.99 | 0.025868 | 0.028793 | 0.030343 | 0.027595 | 999.99 | 8 | 0 | 0.030383 | 999.99 | 0.71665 | 0.75192 | 0.75369 | 0.7561 | 999.99 | 4 | 0.71665 | 0.72
26 | Aug | 0.026182 | 999.99 | 0.029362 | 0.037135 | 0.02736 | 999.99 | 12 | 0 | 0.038548 | 0.73143 | 999.99 | 0.72048 | 0.74374 | 0.76382 | 999.99 | 8 | 0.72048 | 0.72
27 | Aug | 0.033366 | 999.99 | 0.028577 | 0.035408 | 0.029892 | 999.99 | 0 | 0 | 0.037567 | 0.73343 | 999.99 | 0.7226 | 0.7375 | 0.76382 | 999.99 | 8 | 0.7226 | 0.72
28 | Aug | 999.99 | 999.99 | 999.99 | 0.03054 | 0.030285 | 999.99 | 12 | 0 | 0.034289 | 999.99 | 999.99 | 999.99 | 0.75016 | 0.75016 | 999.99 | 16 | 0.75016 | 0.75
29 | Aug | 999.99 | 0.028812 | 0.03951 | 0.033916 | 999.99 | 0.030304 | 8 | 0 | 0.039844 | 999.99 | 0.75557 | 0.74639 | 0.76653 | 999.99 | 0.72442 | 20 | 0.72442 | 0.72
30 | Aug | 999.99 | 999.99 | 0.045477 | 0.040511 | 999.99 | 999.99 | 8 | 0 | 0.045477 | 999.99 | 999.99 | 0.72171 | 0.7425 | 999.99 | 999.99 | 8 | 0.72171 | 0.72
31 | Aug | 0.031148 | 0.027693 | 0.030383 | 0.029951 | 999.99 | 999.99 | 12 | 0 | 0.033013 | 0.71164 | 0.73979 | 0.76211 | 0.77766 | 999.99 | 999.99 | 4 | 0.73979 | 0.74