## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Dec_22
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.02 | 0.02 | OFF | OFF | 0.02 | 0.02 | 0.02
2 | 0.02 | 0.03 | OFF | 0.03262 | 0.02 | OFF | 0.03
3 | 0.02 | OFF | 0.032463 | 0.03 | 0.02 | 0.02 | 0.03
4 | 0.02 | OFF | 0.03 | 0.02 | 0.02 | OFF | 0.03
5 | OFF | OFF | 0.023944 | 0.027674 | 0.02 | OFF | 0.028969
6 | 0.02 | 0.02 | 0.02 | OFF | 0.024553 | 0.024396 | 0.02
7 | 0.024729 | OFF | OFF | 0.023081 | OFF | 0.02 | 0.02
8 | 0.022806 | OFF | OFF | 0.024101 | OFF | 0.022668 | 0.02
9 | 0.023669 | OFF | OFF | 0.034348 | 0.022845 | 0.031874 | 0.034348
10 | OFF | OFF | 0.02 | 0.029598 | OFF | 0.02 | 0.032208
11 | 0.02 | OFF | OFF | OFF | OFF | 0.02 | 0.02
12 | 0.02416 | OFF | 0.02 | OFF | OFF | 0.02 | 0.02
13 | 0.023414 | OFF | OFF | 0.024199 | OFF | 0.024396 | 0.02
14 | 0.02 | OFF | 0.02 | OFF | 0.024533 | 0.03 | 0.03
15 | OFF | OFF | 0.043888 | 0.02 | OFF | 0.02 | 0.04
16 | 0.02 | OFF | 0.02 | 0.022865 | 0.024847 | OFF | 0.02
17 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
18 | 0.02 | OFF | 0.02 | 0.02 | 0.03 | OFF | 0.03
19 | 0.04 | OFF | 0.04 | 0.021078 | OFF | 0.024062 | 0.04
20 | OFF | OFF | 0.024239 | 0.021903 | OFF | OFF | 0.024514
21 | OFF | OFF | 0.023827 | 0.024514 | 0.022708 | OFF | 0.02
22 | 0.023061 | OFF | 0.022668 | 0.023375 | OFF | 0.023159 | 0.02
23 | OFF | OFF | 0.02 | 0.023081 | OFF | 0.02 | 0.02
24 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
25 | 0.024808 | OFF | 0.023297 | 0.023768 | 0.02 | OFF | 0.02
26 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
27 | 0.02 | OFF | OFF | 0.02 | OFF | 0.023238 | 0.02
28 | OFF | OFF | 0.02 | 0.024003 | 0.02 | OFF | 0.02
29 | OFF | 0.03 | 0.02 | OFF | OFF | 0.02 | 0.03
30 | OFF | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02
31 | 0.02 | OFF | OFF | OFF | OFF | OFF | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:01/01/2023
[5 empty] | PHONE #: (541)265-2610 |  |  | CERT #:T-269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Dec_22 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 20:00 | 0.91 | 111 | 101.01 | 8.3 | 7.25 | 23.3119 | YES | 785
2 / 12:00 | 0.86 | 111 | 95.46 | 8.1 | 7.37 | 24.5109 | YES | 756
3 / 20:00 | 0.78 | 111 | 86.58 | 8 | 7.37 | 24.4505 | YES | 725
4 / 8:00 | 0.78 | 111 | 86.58 | 8 | 7.49 | 25.5176 | YES | 744
5 / 8:00 | 0.79 | 111 | 87.69 | 8 | 7.42 | 24.9176 | YES | 797
6 / 20:00 | 0.79 | 111 | 87.69 | 8 | 7.42 | 24.9176 | YES | 806
7 / 20:00 | 0.77 | 111 | 85.47 | 8.1 | 7.37 | 24.2604 | YES | 790
8 / 12:00 | 0.78 | 111 | 86.58 | 8.2 | 7.59 | 26.0932 | YES | 790
9 / 12:00 | 0.79 | 111 | 87.69 | 8.2 | 7.42 | 24.5871 | YES | 786
10 / 8:00 | 0.8 | 111 | 88.8 | 8.2 | 7.51 | 25.4168 | YES | 734
11 / 20:00 | 0.81 | 111 | 89.91 | 8.2 | 7.52 | 25.5368 | YES | 744
12 / 20:00 | 0.81 | 111 | 89.91 | 8.8 | 7.39 | 23.428 | YES | 746
13 / 20:00 | 0.81 | 111 | 89.91 | 8.3 | 7.34 | 23.7944 | YES | 773
14 / 16:00 | 0.8 | 111 | 88.8 | 8.7 | 7.29 | 22.7394 | YES | 758
15 / 8:00 | 0.79 | 111 | 87.69 | 8.4 | 7.4 | 24.0899 | YES | 840
16 / 8:00 | 0.79 | 111 | 87.69 | 8.3 | 7.34 | 23.7403 | YES | 823
17 / 24:00 | 1.44 | 111 | 159.84 | 8.3 | 7.67 | 28.7826 | YES | 838
18 / 16:00 | 1.5 | 111 | 166.5 | 8.1 | 7.74 | 30.1309 | YES | 853
19 / 20:00 | 1.16 | 111 | 128.76 | 8.3 | 7.51 | 26.3119 | YES | 799
20 / 12:00 | 1.07 | 111 | 118.77 | 8.2 | 7.54 | 26.4994 | YES | 773
21 / 16:00 | 0.99 | 111 | 109.89 | 8.1 | 7.51 | 26.1515 | YES | 792
22 / 20:00 | 0.95 | 111 | 105.45 | 8 | 7.59 | 26.9683 | YES | 854
23 / 20:00 | 0.91 | 111 | 101.01 | 7.7 | 7.48 | 26.3332 | YES | 857
24 / 8:00 | 0.91 | 111 | 101.01 | 7.4 | 7.6 | 28.052 | YES | 858
25 / 8:00 | 0.9 | 111 | 99.9 | 7.6 | 7.57 | 27.3481 | YES | 815
26 / 16:00 | 0.91 | 111 | 101.01 | 7.9 | 7.65 | 27.6136 | YES | 858
27 / 20:00 | 0.86 | 111 | 95.46 | 8.5 | 7.64 | 26.2749 | YES | 794
28 / 8:00 | 0.86 | 111 | 95.46 | 8.4 | 7.57 | 25.7982 | YES | 813
29 / 4:00 | 0.89 | 111 | 98.79 | 8.4 | 7.62 | 26.354 | YES | 802
30 / 8:00 | 0.9 | 111 | 99.9 | 8.5 | 7.58 | 25.8359 | YES | 857
31 / 24:00 | 0.92 | 111 | 102.12 | 8.7 | 7.55 | 25.2788 | YES | 822
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Dec | 0.028498 | 0.025632 | 999.99 | 999.99 | 0.026908 | 0.027811 | 20 | 0 | 0.030579 | 0.93948 | 0.98429 | 999.99 | 999.99 | 0.95367 | 0.91587 | 20 | 0.91587 | 0.92
2 | Dec | 0.031443 | 0.037999 | 999.99 | 0.03262 | 0.027693 | 999.99 | 4 | 0 | 0.037999 | 0.89685 | 0.88354 | 999.99 | 0.85839 | 0.86399 | 999.99 | 12 | 0.85839 | 0.86
3 | Dec | 0.034544 | 999.99 | 0.032463 | 0.029342 | 0.026378 | 0.028223 | 0 | 0 | 0.036154 | 0.82023 | 999.99 | 0.79892 | 0.80274 | 0.80475 | 0.77548 | 20 | 0.77548 | 0.78
4 | Dec | 0.026928 | 999.99 | 0.034897 | 0.026084 | 0.025377 | 999.99 | 8 | 0 | 0.036213 | 0.79314 | 999.99 | 0.78543 | 0.79067 | 0.8114 | 999.99 | 8 | 0.78543 | 0.79
5 | Dec | 999.99 | 999.99 | 0.023944 | 0.027674 | 0.027301 | 999.99 | 16 | 0 | 0.028969 | 999.99 | 999.99 | 0.79044 | 0.82383 | 0.82388 | 999.99 | 8 | 0.79044 | 0.79
6 | Dec | 0.027811 | 0.027262 | 0.028675 | 999.99 | 0.024553 | 0.024396 | 8 | 0 | 0.028753 | 0.81417 | 0.81258 | 0.80451 | 999.99 | 0.78325 | 0.79138 | 20 | 0.78325 | 0.78
7 | Dec | 0.024729 | 999.99 | 999.99 | 0.023081 | 999.99 | 0.025888 | 0 | 0 | 0.026751 | 0.79939 | 999.99 | 999.99 | 0.77672 | 999.99 | 0.76906 | 20 | 0.76906 | 0.77
8 | Dec | 0.022806 | 999.99 | 999.99 | 0.024101 | 999.99 | 0.022668 | 12 | 0 | 0.026771 | 0.79526 | 999.99 | 999.99 | 0.78985 | 999.99 | 0.79267 | 12 | 0.78985 | 0.79
9 | Dec | 0.023669 | 999.99 | 999.99 | 0.034348 | 0.022845 | 0.031874 | 12 | 0 | 0.034348 | 0.81387 | 999.99 | 999.99 | 0.79409 | 0.80333 | 0.80351 | 12 | 0.79409 | 0.79
10 | Dec | 999.99 | 999.99 | 0.028734 | 0.029598 | 999.99 | 0.028263 | 12 | 0 | 0.032208 | 999.99 | 999.99 | 0.79497 | 0.79591 | 999.99 | 0.80722 | 8 | 0.79497 | 0.79
11 | Dec | 0.026457 | 999.99 | 999.99 | 999.99 | 999.99 | 0.025044 | 0 | 0 | 0.028184 | 0.81964 | 999.99 | 999.99 | 999.99 | 999.99 | 0.81864 | 20 | 0.81864 | 0.82
12 | Dec | 0.02416 | 999.99 | 0.028557 | 999.99 | 999.99 | 0.026025 | 8 | 0 | 0.028616 | 0.82318 | 999.99 | 0.80957 | 999.99 | 999.99 | 0.80716 | 20 | 0.80716 | 0.81
13 | Dec | 0.023414 | 999.99 | 999.99 | 0.024199 | 999.99 | 0.024396 | 20 | 0 | 0.027635 | 0.82683 | 999.99 | 999.99 | 0.8144 | 999.99 | 0.80581 | 20 | 0.80581 | 0.81
14 | Dec | 0.029539 | 999.99 | 0.030795 | 999.99 | 0.024533 | 0.044064 | 20 | 0 | 0.044162 | 0.82347 | 999.99 | 0.80963 | 999.99 | 0.80215 | 0.81535 | 16 | 0.80215 | 0.8
15 | Dec | 999.99 | 999.99 | 0.043888 | 0.026712 | 999.99 | 0.030952 | 8 | 0 | 0.046204 | 999.99 | 999.99 | 0.78908 | 0.79897 | 999.99 | 0.81287 | 8 | 0.78908 | 0.79
16 | Dec | 0.029872 | 999.99 | 0.027674 | 0.022865 | 0.024847 | 999.99 | 0 | 0 | 0.030127 | 0.8028 | 999.99 | 0.77819 | 0.79291 | 0.88607 | 999.99 | 8 | 0.77819 | 0.78
17 | Dec | 0.037685 | 0.025593 | 0.026791 | 0.022767 | 0.02683 | 999.99 | 8 | 0 | 0.027006 | 1.4357 | 1.7332 | 1.9243 | 2.0694 | 1.9818 | 999.99 | 4 | 1.7332 | 1.73
18 | Dec | 0.027301 | 999.99 | 0.029696 | 0.035545 | 0.045399 | 999.99 | 16 | 0 | 0.045477 | 1.8605 | 999.99 | 1.7658 | 1.6321 | 1.4949 | 999.99 | 16 | 1.4949 | 1.49
19 | Dec | 0.056902 | 999.99 | 0.045988 | 0.021078 | 999.99 | 0.024062 | 8 | 0 | 0.046479 | 1.3711 | 999.99 | 1.2877 | 1.2292 | 999.99 | 1.1546 | 20 | 1.1546 | 1.15
20 | Dec | 999.99 | 999.99 | 0.024239 | 0.021903 | 999.99 | 999.99 | 12 | 0 | 0.024514 | 999.99 | 999.99 | 1.0984 | 1.0791 | 999.99 | 999.99 | 12 | 1.0791 | 1.08
21 | Dec | 999.99 | 999.99 | 0.023827 | 0.024514 | 0.022708 | 999.99 | 8 | 0 | 0.02522 | 999.99 | 999.99 | 1.0014 | 0.99813 | 1.0046 | 999.99 | 16 | 0.99813 | 1
22 | Dec | 0.023061 | 999.99 | 0.022668 | 0.023375 | 999.99 | 0.023159 | 12 | 0 | 0.026496 | 0.96898 | 999.99 | 0.96751 | 0.9588 | 999.99 | 0.94519 | 20 | 0.94519 | 0.95
23 | Dec | 999.99 | 999.99 | 0.026221 | 0.023081 | 999.99 | 0.026123 | 8 | 0 | 0.026496 | 999.99 | 999.99 | 0.93359 | 0.92599 | 999.99 | 0.91139 | 20 | 0.91139 | 0.91
24 | Dec | 999.99 | 999.99 | 0.026437 | 0.025456 | 999.99 | 999.99 | 8 | 0 | 0.026516 | 999.99 | 999.99 | 0.90709 | 0.92358 | 999.99 | 999.99 | 8 | 0.90709 | 0.91
25 | Dec | 0.024808 | 999.99 | 0.023297 | 0.023768 | 0.027399 | 999.99 | 16 | 0 | 0.027949 | 0.91775 | 999.99 | 0.9035 | 0.91475 | 0.92276 | 999.99 | 8 | 0.9035 | 0.9
26 | Dec | 999.99 | 999.99 | 999.99 | 0.027124 | 0.029087 | 999.99 | 16 | 0 | 0.031011 | 999.99 | 999.99 | 999.99 | 0.90521 | 0.9065 | 999.99 | 16 | 0.90521 | 0.91
27 | Dec | 0.033131 | 999.99 | 999.99 | 0.025632 | 999.99 | 0.023238 | 12 | 0 | 0.027713 | 0.90144 | 999.99 | 999.99 | 0.8694 | 999.99 | 0.86687 | 20 | 0.86687 | 0.87
28 | Dec | 999.99 | 999.99 | 0.025102 | 0.024003 | 0.02734 | 999.99 | 16 | 0 | 0.028322 | 999.99 | 999.99 | 0.87235 | 0.88365 | 0.89955 | 999.99 | 8 | 0.87235 | 0.87
29 | Dec | 999.99 | 0.047224 | 0.026791 | 999.99 | 999.99 | 0.031384 | 4 | 0 | 0.050699 | 999.99 | 0.87989 | 0.89944 | 999.99 | 999.99 | 0.89037 | 4 | 0.87989 | 0.88
30 | Dec | 999.99 | 999.99 | 0.034407 | 999.99 | 0.025377 | 0.02838 | 8 | 0 | 0.034446 | 999.99 | 999.99 | 0.88736 | 999.99 | 0.90762 | 0.91057 | 8 | 0.88736 | 0.89
31 | Dec | 0.026476 | 999.99 | 999.99 | 999.99 | 999.99 | 999.99 | 0 | 0 | 0.030834 | 0.91074 | 999.99 | 999.99 | 999.99 | 999.99 | 999.99 | 24 | 0.92 | 0.92