## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Feb_23
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | 0.020097 | 0.01835 | 0.017251 | OFF | 0.021
2 | OFF | OFF | 0.019331 | OFF | 0.015229 | 0.017643 | 0.021275
3 | 0.01886 | OFF | 0.021746 | 0.023081 | OFF | OFF | 0.02314
4 | 0.03 | OFF | 0.021864 | 0.042592 | 0.017781 | OFF | 0.043789
5 | 0.019194 | OFF | 0.018448 | 0.017329 | OFF | OFF | 0.020843
6 | 0.017859 | OFF | 0.018036 | 0.020961 | OFF | OFF | 0.020961
7 | OFF | OFF | 0.018487 | 0.019567 | 0.016721 | 0.019135 | 0.021059
8 | OFF | OFF | 0.017879 | 0.020921 | OFF | OFF | 0.023925
9 | OFF | OFF | 0.017113 | 0.024729 | 0.020568 | OFF | 0.024749
10 | OFF | OFF | 0.021157 | 0.018448 | 0.017879 | OFF | 0.021864
11 | OFF | OFF | 0.01731 | 0.02049 | 0.019646 | OFF | 0.020941
12 | OFF | OFF | 0.020568 | 0.017526 | 0.019194 | OFF | 0.020823
13 | OFF | OFF | 0.019253 | 0.018762 | 0.021471 | OFF | 0.024199
14 | OFF | OFF | 0.0189 | 0.021255 | 0.018271 | OFF | 0.022394
15 | OFF | OFF | OFF | 0.018213 | 0.020509 | OFF | 0.021726
16 | OFF | OFF | 0.021432 | 0.019763 | 0.018487 | OFF | 0.022099
17 | OFF | OFF | 0.018389 | 0.019842 | 0.021785 | OFF | 0.022138
18 | OFF | OFF | 0.021864 | 0.024631 | 0.020627 | 0.019842 | 0.02
19 | OFF | OFF | 0.021667 | 0.022747 | OFF | OFF | 0.023827
20 | OFF | OFF | 0.022197 | 0.024082 | OFF | OFF | 0.024847
21 | OFF | 0.021864 | 0.018782 | OFF | 0.021177 | OFF | 0.022747
22 | OFF | OFF | 0.023669 | 0.021196 | 0.02 | OFF | 0.02
23 | OFF | OFF | OFF | 0.02 | 0.024631 | 0.02 | 0.02
24 | OFF | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02
25 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
26 | 0.03 | 0.028086 | OFF | 0.032247 | 0.03 | OFF | 0.03
27 | OFF | OFF | OFF | 0.03372 | 0.034328 | 0.033464 | 0.034328
28 | OFF | OFF | OFF | 0.031737 | 0.028263 | OFF | 0.032228
29
30
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:03/01/2023
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Feb_23 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 16:00 | 0.78 | 111 | 86.58 | 8.4 | 7.58 | 25.654 | YES | 786
2 / 8:00 | 0.82 | 111 | 91.02 | 7.9 | 7.88 | 29.6879 | YES | 777
3 / 8:00 | 0.97 | 111 | 107.67 | 8.4 | 7.69 | 27.2733 | YES | 795
4 / 16:00 | 0.93 | 111 | 103.23 | 8.3 | 7.55 | 25.9949 | YES | 840
5 / 12:00 | 0.9 | 111 | 99.9 | 8.4 | 7.49 | 25.1877 | YES | 837
6 / 12:00 | 0.87 | 111 | 96.57 | 8.1 | 7.39 | 24.714 | YES | 829
7 / 20:00 | 0.82 | 111 | 91.02 | 8.3 | 7.32 | 23.6533 | YES | 863
8 / 12:00 | 0.8 | 111 | 88.8 | 8.1 | 7.51 | 25.5875 | YES | 865
9 / 8:00 | 0.78 | 111 | 86.58 | 8.5 | 7.41 | 23.9877 | YES | 808
10 / 8:00 | 0.78 | 111 | 86.58 | 8.4 | 7.38 | 23.8924 | YES | 798
11 / 8:00 | 0.76 | 111 | 84.36 | 8.4 | 7.27 | 22.9283 | YES | 786
12 / 8:00 | 0.75 | 111 | 83.25 | 8.7 | 7.25 | 22.2945 | YES | 772
13 / 8:00 | 0.76 | 111 | 84.36 | 8.8 | 7.4 | 23.3777 | YES | 856
14 / 8:00 | 0.75 | 111 | 83.25 | 7.7 | 7.38 | 24.9481 | YES | 822
15 / 12:00 | 0.77 | 111 | 85.47 | 7.6 | 7.42 | 25.5345 | YES | 839
16 / 8:00 | 0.76 | 111 | 84.36 | 7.6 | 7.4 | 25.324 | YES | 821
17 / 8:00 | 0.75 | 111 | 83.25 | 7.7 | 7.31 | 24.3349 | YES | 833
18 / 8:00 | 0.75 | 111 | 83.25 | 7.9 | 7.33 | 24.1839 | YES | 765
19 / 8:00 | 0.77 | 111 | 85.47 | 8 | 7.35 | 24.2498 | YES | 802
20 / 12:00 | 0.77 | 111 | 85.47 | 8.1 | 7.34 | 24.0035 | YES | 784
21 / 4:00 | 0.75 | 111 | 83.25 | 8.1 | 7.47 | 25.0812 | YES | 805
22 / 8:00 | 0.76 | 111 | 84.36 | 8.1 | 7.58 | 26.115 | YES | 803
23 / 12:00 | 0.78 | 111 | 86.58 | 7.6 | 7.59 | 27.1666 | YES | 871
24 / 12:00 | 0.77 | 111 | 85.47 | 7.3 | 7.62 | 27.9894 | YES | 821
25 / 12:00 | 0.77 | 111 | 85.47 | 6.9 | 7.34 | 26.007 | YES | 854
26 / 16:00 | 0.76 | 111 | 84.36 | 7.4 | 7.18 | 23.734 | YES | 831
27 / 12:00 | 0.77 | 111 | 85.47 | 7.1 | 7.32 | 25.4784 | YES | 824
28 / 12:00 | 0.77 | 111 | 85.47 | 7.2 | 7.34 | 25.4896 | YES | 790
29 |  | 111 |  |  |  |  | NO
30 |  | 111 |  |  |  |  | NO
31 |  | 111 |  |  |  |  | NO
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Feb | 999.99 | 999.99 | 0.020097 | 0.01835 | 0.017251 | 999.99 | 8 | 0 | 0.021 | 999.99 | 999.99 | 0.77854 | 0.78732 | 0.78054 | 999.99 | 16 | 0.77854 | 0.78
2 | Feb | 999.99 | 999.99 | 0.019331 | 999.99 | 0.015229 | 0.017643 | 20 | 0 | 0.021275 | 999.99 | 999.99 | 0.82235 | 999.99 | 0.88642 | 0.93553 | 8 | 0.82235 | 0.82
3 | Feb | 0.01886 | 999.99 | 0.021746 | 0.023081 | 999.99 | 999.99 | 12 | 0 | 0.02314 | 0.9797 | 999.99 | 0.96939 | 0.98041 | 999.99 | 999.99 | 8 | 0.96939 | 0.97
4 | Feb | 0.036939 | 999.99 | 0.021864 | 0.042592 | 0.017781 | 999.99 | 12 | 0 | 0.043789 | 0.95803 | 999.99 | 0.94307 | 0.9353 | 0.93848 | 999.99 | 16 | 0.9353 | 0.94
5 | Feb | 0.019194 | 999.99 | 0.018448 | 0.017329 | 999.99 | 999.99 | 12 | 0 | 0.020843 | 0.92329 | 999.99 | 0.90374 | 0.91198 | 999.99 | 999.99 | 12 | 0.90374 | 0.9
6 | Feb | 0.017859 | 999.99 | 0.018036 | 0.020961 | 999.99 | 999.99 | 12 | 0 | 0.020961 | 0.87541 | 999.99 | 0.87223 | 0.86493 | 999.99 | 999.99 | 12 | 0.86493 | 0.86
7 | Feb | 999.99 | 999.99 | 0.018487 | 0.019567 | 0.016721 | 0.019135 | 20 | 0 | 0.021059 | 999.99 | 999.99 | 0.83531 | 0.83825 | 0.83254 | 0.83048 | 20 | 0.83048 | 0.83
8 | Feb | 999.99 | 999.99 | 0.017879 | 0.020921 | 999.99 | 999.99 | 8 | 0 | 0.023925 | 999.99 | 999.99 | 0.80098 | 0.79756 | 999.99 | 999.99 | 12 | 0.79756 | 0.8
9 | Feb | 999.99 | 999.99 | 0.017113 | 0.024729 | 0.020568 | 999.99 | 12 | 0 | 0.024749 | 999.99 | 999.99 | 0.78402 | 0.79662 | 0.79485 | 999.99 | 8 | 0.78402 | 0.78
10 | Feb | 999.99 | 999.99 | 0.021157 | 0.018448 | 0.017879 | 999.99 | 8 | 0 | 0.021864 | 999.99 | 999.99 | 0.77507 | 0.79403 | 0.79791 | 999.99 | 8 | 0.77507 | 0.78
11 | Feb | 999.99 | 999.99 | 0.01731 | 0.02049 | 0.019646 | 999.99 | 16 | 0 | 0.020941 | 999.99 | 999.99 | 0.76771 | 0.7796 | 0.77831 | 999.99 | 8 | 0.76771 | 0.77
12 | Feb | 999.99 | 999.99 | 0.020568 | 0.017526 | 0.019194 | 999.99 | 16 | 0 | 0.020823 | 999.99 | 999.99 | 0.76223 | 0.76547 | 0.78096 | 999.99 | 8 | 0.76223 | 0.76
13 | Feb | 999.99 | 999.99 | 0.019253 | 0.018762 | 0.021471 | 999.99 | 16 | 0 | 0.024199 | 999.99 | 999.99 | 0.76105 | 0.76541 | 0.77995 | 999.99 | 8 | 0.76105 | 0.76
14 | Feb | 999.99 | 999.99 | 0.0189 | 0.021255 | 0.018271 | 999.99 | 12 | 0 | 0.022394 | 999.99 | 999.99 | 0.75911 | 0.77607 | 0.78054 | 999.99 | 8 | 0.75911 | 0.76
15 | Feb | 999.99 | 999.99 | 999.99 | 0.018213 | 0.020509 | 999.99 | 12 | 0 | 0.021726 | 999.99 | 999.99 | 999.99 | 0.77212 | 0.77012 | 999.99 | 12 | 0.77012 | 0.77
16 | Feb | 999.99 | 999.99 | 0.021432 | 0.019763 | 0.018487 | 999.99 | 8 | 0 | 0.022099 | 999.99 | 999.99 | 0.75793 | 0.78154 | 0.78149 | 999.99 | 8 | 0.75793 | 0.76
17 | Feb | 999.99 | 999.99 | 0.018389 | 0.019842 | 0.021785 | 999.99 | 12 | 0 | 0.022138 | 999.99 | 999.99 | 0.75522 | 0.77136 | 0.77577 | 999.99 | 8 | 0.75522 | 0.76
18 | Feb | 999.99 | 999.99 | 0.021864 | 0.024631 | 0.020627 | 0.019842 | 12 | 0 | 0.026869 | 999.99 | 999.99 | 0.7597 | 0.77742 | 0.79044 | 0.80027 | 8 | 0.7597 | 0.76
19 | Feb | 999.99 | 999.99 | 0.021667 | 0.022747 | 999.99 | 999.99 | 8 | 0 | 0.023827 | 999.99 | 999.99 | 0.77065 | 0.78861 | 999.99 | 999.99 | 8 | 0.77065 | 0.77
20 | Feb | 999.99 | 999.99 | 0.022197 | 0.024082 | 999.99 | 999.99 | 12 | 0 | 0.024847 | 999.99 | 999.99 | 0.77683 | 0.76606 | 999.99 | 999.99 | 12 | 0.76606 | 0.77
21 | Feb | 999.99 | 0.021864 | 0.018782 | 999.99 | 0.021177 | 999.99 | 4 | 0 | 0.022747 | 999.99 | 0.73779 | 0.76058 | 999.99 | 0.77253 | 999.99 | 4 | 0.73779 | 0.74
22 | Feb | 999.99 | 999.99 | 0.023669 | 0.021196 | 0.025672 | 999.99 | 16 | 0 | 0.027262 | 999.99 | 999.99 | 0.75552 | 0.78938 | 0.79927 | 999.99 | 8 | 0.75552 | 0.76
23 | Feb | 999.99 | 999.99 | 999.99 | 0.027752 | 0.024631 | 0.026496 | 12 | 0 | 0.027752 | 999.99 | 999.99 | 999.99 | 0.78431 | 0.80639 | 0.7995 | 12 | 0.78431 | 0.78
24 | Feb | 999.99 | 999.99 | 999.99 | 0.029009 | 0.028871 | 0.026359 | 20 | 0 | 0.035408 | 999.99 | 999.99 | 999.99 | 0.772 | 0.79014 | 0.78849 | 12 | 0.772 | 0.77
25 | Feb | 999.99 | 999.99 | 0.031168 | 0.025809 | 0.027046 | 999.99 | 8 | 0 | 0.031168 | 999.99 | 999.99 | 0.76453 | 0.78425 | 0.78561 | 999.99 | 12 | 0.76453 | 0.76
26 | Feb | 0.037567 | 0.028086 | 999.99 | 0.032247 | 0.035604 | 999.99 | 16 | 0 | 0.0358 | 0.76193 | 0.76623 | 999.99 | 0.76877 | 0.75775 | 999.99 | 16 | 0.75775 | 0.76
27 | Feb | 999.99 | 999.99 | 999.99 | 0.03372 | 0.034328 | 0.033464 | 16 | 0 | 0.034328 | 999.99 | 999.99 | 999.99 | 0.75822 | 0.77672 | 0.78826 | 12 | 0.75822 | 0.76
28 | Feb | 999.99 | 999.99 | 999.99 | 0.031737 | 0.028263 | 999.99 | 16 | 0 | 0.032228 | 999.99 | 999.99 | 999.99 | 0.76641 | 0.78325 | 999.99 | 12 | 0.76641 | 0.77