## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Mar_23
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | OFF | 0.02 | 0.02 | 0.02
2 | 0.02 | OFF | OFF | 0.027831 | 0.02 | OFF | 0.029578
3 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.028243 | 0.03
4 | OFF | OFF | 0.031423 | 0.025888 | 0.02999 | OFF | 0.031423
5 | OFF | OFF | 0.026594 | 0.03 | 0.02683 | OFF | 0.03315
6 | OFF | OFF | 0.026692 | 0.03 | 0.026123 | OFF | 0.027497
7 | OFF | OFF | 0.02 | 0.024671 | 0.02 | OFF | 0.02
8 | OFF | OFF | OFF | 0.021491 | 0.022767 | OFF | 0.02
9 | OFF | OFF | 0.02 | 0.024494 | 0.02 | OFF | 0.02
10 | OFF | OFF | 0.02 | OFF | 0.02 | 0.023257 | 0.02
11 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
12 | OFF | OFF | 0.03 | 0.024514 | 0.022472 | OFF | 0.026771
13 | OFF | OFF | 0.022394 | 0.02 | 0.02 | OFF | 0.02
14 | OFF | OFF | 0.02 | 0.02 | 0.026594 | OFF | 0.028812
15 | OFF | OFF | 0.03 | 0.03 | 0.026869 | OFF | 0.034799
16 | OFF | OFF | 0.026045 | 0.022747 | OFF | OFF | 0.026045
17 | OFF | OFF | 0.02 | 0.024965 | 0.02 | OFF | 0.02
18 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
19 | OFF | OFF | OFF | 0.02 | 0.024847 | OFF | 0.023
20 | OFF | OFF | OFF | 0.023905 | 0.024435 | OFF | 0.02
21 | OFF | OFF | 0.02 | OFF | OFF | 0.021491 | 0.02
22 | OFF | OFF | 0.022688 | 0.02 | 0.02 | OFF | 0.02
23 | OFF | OFF | 0.02 | 0.02 | 0.026182 | OFF | 0.029833
24 | OFF | OFF | 0.03 | 0.02787 | 0.02 | OFF | 0.028027
25 | OFF | OFF | 0.026261 | 0.026967 | 0.02 | OFF | 0.02734
26 | OFF | OFF | 0.023512 | 0.024082 | OFF | OFF | 0.02
27 | OFF | OFF | 0.03 | 0.03 | OFF | 0.02 | 0.03
28 | OFF | OFF | 0.03 | 0.03 | 0.02 | 0.02 | 0.03
29 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
30 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
31 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Mar_23 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 16:00 | 0.78 | 111 | 86.58 | 6.7 | 7.34 | 26.3887 | YES | 792
2 / 16:00 | 0.76 | 111 | 84.36 | 6.8 | 7.37 | 26.4341 | YES | 779
3 / 8:00 | 0.73 | 111 | 81.03 | 6.9 | 7.27 | 25.2494 | YES | 776
4 / 8:00 | 0.74 | 111 | 82.14 | 7 | 7.3 | 25.3798 | YES | 817
5 / 8:00 | 0.73 | 111 | 81.03 | 6.9 | 7.28 | 25.3396 | YES | 855
6 / 8:00 | 0.75 | 111 | 83.25 | 6.9 | 7.22 | 24.8607 | YES | 854
7 / 8:00 | 0.76 | 111 | 84.36 | 7.1 | 7.32 | 25.4492 | YES | 828
8 / 12:00 | 0.75 | 111 | 83.25 | 7 | 7.54 | 27.6879 | YES | 828
9 / 8:00 | 0.73 | 111 | 81.03 | 7 | 7.65 | 28.7391 | YES | 824
10 / 20:00 | 0.74 | 111 | 82.14 | 7 | 7.52 | 27.4581 | YES | 786
11 / 12:00 | 0.73 | 111 | 81.03 | 7 | 7.5 | 27.2303 | YES | 768
12 / 8:00 | 0.72 | 111 | 79.92 | 7.1 | 7.44 | 26.4421 | YES | 823
13 / 8:00 | 0.74 | 111 | 82.14 | 7.3 | 7.44 | 26.1496 | YES | 782
14 / 8:00 | 0.74 | 111 | 82.14 | 7.3 | 7.48 | 26.5264 | YES | 816
15 / 8:00 | 0.74 | 111 | 82.14 | 7.5 | 7.41 | 25.5265 | YES | 841
16 / 8:00 | 0.72 | 111 | 79.92 | 7.6 | 7.4 | 25.2083 | YES | 823
17 / 8:00 | 0.76 | 111 | 84.36 | 7.7 | 7.33 | 24.5364 | YES | 848
18 / 8:00 | 0.77 | 111 | 85.47 | 7.8 | 7.32 | 24.3147 | YES | 758
19 / 12:00 | 0.77 | 111 | 85.47 | 8 | 7.24 | 23.3228 | YES | 816
20 / 8:00 | 0.76 | 111 | 84.36 | 8 | 7.3 | 23.7964 | YES | 823
21 / 20:00 | 0.73 | 111 | 81.03 | 7.9 | 7.35 | 24.3007 | YES | 787
22 / 8:00 | 0.74 | 111 | 82.14 | 7.7 | 7.36 | 24.7429 | YES | 770
23 / 8:00 | 0.75 | 111 | 83.25 | 8.2 | 7.34 | 23.7901 | YES | 850
24 / 8:00 | 0.77 | 111 | 85.47 | 8.2 | 7.32 | 23.676 | YES | 833
25 / 8:00 | 0.75 | 111 | 83.25 | 8 | 7.25 | 23.3523 | YES | 824
26 / 8:00 | 0.75 | 111 | 83.25 | 8 | 7.23 | 23.1877 | YES | 829
27 / 8:00 | 0.73 | 111 | 81.03 | 8.2 | 7.31 | 23.4852 | YES | 829
28 / 8:00 | 0.73 | 111 | 81.03 | 8.2 | 7.36 | 23.9048 | YES | 804
29 / 12:00 | 0.75 | 111 | 83.25 | 8.2 | 7.54 | 25.5434 | YES | 773
30 / 20:00 | 0.75 | 111 | 83.25 | 8.5 | 7.6 | 25.5772 | YES | 762
31 / 8:00 | 0.75 | 111 | 83.25 | 8.5 | 7.49 | 24.5946 | YES | 787
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Mar | 999.99 | 999.99 | 999.99 | 999.99 | 0.028773 | 0.028322 | 20 | 0 | 0.029323 | 999.99 | 999.99 | 999.99 | 999.99 | 0.78325 | 0.79903 | 16 | 0.78325 | 0.78
2 | Mar | 0.026437 | 999.99 | 999.99 | 0.027831 | 0.028498 | 999.99 | 12 | 0 | 0.029578 | 0.79132 | 999.99 | 999.99 | 0.769 | 0.76335 | 999.99 | 16 | 0.76335 | 0.76
3 | Mar | 999.99 | 999.99 | 0.025397 | 0.034623 | 0.028086 | 0.028243 | 20 | 0 | 0.042337 | 999.99 | 999.99 | 0.73361 | 0.74998 | 0.76323 | 0.75764 | 8 | 0.73361 | 0.73
4 | Mar | 999.99 | 999.99 | 0.031423 | 0.025888 | 0.02999 | 999.99 | 8 | 0 | 0.031423 | 999.99 | 999.99 | 0.73756 | 0.74162 | 0.74527 | 999.99 | 8 | 0.73756 | 0.74
5 | Mar | 999.99 | 999.99 | 0.026594 | 0.024592 | 0.02683 | 999.99 | 12 | 0 | 0.03315 | 999.99 | 999.99 | 0.72542 | 0.75027 | 0.77418 | 999.99 | 8 | 0.72542 | 0.73
6 | Mar | 999.99 | 999.99 | 0.026692 | 0.023728 | 0.026123 | 999.99 | 16 | 0 | 0.027497 | 999.99 | 999.99 | 0.7534 | 0.78496 | 0.79079 | 999.99 | 8 | 0.7534 | 0.75
7 | Mar | 999.99 | 999.99 | 0.025652 | 0.024671 | 0.02522 | 999.99 | 8 | 0 | 0.026182 | 999.99 | 999.99 | 0.76617 | 0.7703 | 0.77259 | 999.99 | 8 | 0.76617 | 0.77
8 | Mar | 999.99 | 999.99 | 999.99 | 0.021491 | 0.022767 | 999.99 | 16 | 0 | 0.026692 | 999.99 | 999.99 | 999.99 | 0.74916 | 0.76252 | 999.99 | 12 | 0.74916 | 0.75
9 | Mar | 999.99 | 999.99 | 0.025907 | 0.024494 | 0.026123 | 999.99 | 16 | 0 | 0.027144 | 999.99 | 999.99 | 0.73803 | 0.74556 | 0.75357 | 999.99 | 8 | 0.73803 | 0.74
10 | Mar | 999.99 | 999.99 | 0.026732 | 999.99 | 0.025515 | 0.023257 | 8 | 0 | 0.026732 | 999.99 | 999.99 | 0.73025 | 999.99 | 0.73296 | 0.75234 | 20 | 0.73025 | 0.73
11 | Mar | 999.99 | 999.99 | 999.99 | 0.025574 | 999.99 | 999.99 | 12 | 0 | 0.026476 | 999.99 | 999.99 | 999.99 | 0.72466 | 999.99 | 999.99 | 12 | 0.72466 | 0.72
12 | Mar | 999.99 | 999.99 | 0.02257 | 0.024514 | 0.022472 | 999.99 | 16 | 0 | 0.026771 | 999.99 | 999.99 | 0.73067 | 0.7597 | 0.76547 | 999.99 | 8 | 0.73067 | 0.73
13 | Mar | 999.99 | 999.99 | 0.022394 | 0.025279 | 999.99 | 999.99 | 12 | 0 | 0.02736 | 999.99 | 999.99 | 0.74474 | 0.75387 | 999.99 | 999.99 | 8 | 0.74474 | 0.74
14 | Mar | 999.99 | 999.99 | 0.026673 | 0.025907 | 0.026594 | 999.99 | 12 | 0 | 0.028812 | 999.99 | 999.99 | 0.73867 | 0.76494 | 0.75981 | 999.99 | 8 | 0.73867 | 0.74
15 | Mar | 999.99 | 999.99 | 0.023473 | 0.024729 | 0.026869 | 999.99 | 8 | 0 | 0.034799 | 999.99 | 999.99 | 0.73178 | 0.7597 | 0.75581 | 999.99 | 8 | 0.73178 | 0.73
16 | Mar | 999.99 | 999.99 | 0.026045 | 0.022747 | 999.99 | 999.99 | 8 | 0 | 0.026045 | 999.99 | 999.99 | 0.72984 | 0.77336 | 999.99 | 999.99 | 8 | 0.72984 | 0.73
17 | Mar | 999.99 | 999.99 | 0.026064 | 0.024965 | 0.02522 | 999.99 | 8 | 0 | 0.026182 | 999.99 | 999.99 | 0.75964 | 0.78796 | 0.78767 | 999.99 | 8 | 0.75964 | 0.76
18 | Mar | 999.99 | 999.99 | 0.026869 | 0.025593 | 0.026202 | 999.99 | 8 | 0 | 0.026869 | 999.99 | 999.99 | 0.76105 | 0.78249 | 0.80675 | 999.99 | 8 | 0.76105 | 0.76
19 | Mar | 999.99 | 999.99 | 0.026398 | 0.026319 | 0.024847 | 999.99 | 8 | 0 | 0.03001 | 999.99 | 999.99 | 0.77436 | 0.78549 | 0.78667 | 999.99 | 12 | 0.77436 | 0.77
20 | Mar | 999.99 | 999.99 | 0.025632 | 0.023905 | 0.024435 | 999.99 | 16 | 0 | 0.027772 | 999.99 | 999.99 | 0.75345 | 0.76747 | 0.76329 | 999.99 | 8 | 0.75345 | 0.75
21 | Mar | 999.99 | 999.99 | 0.025966 | 999.99 | 999.99 | 0.021491 | 8 | 0 | 0.026692 | 999.99 | 999.99 | 0.74021 | 999.99 | 999.99 | 0.73655 | 20 | 0.73655 | 0.74
22 | Mar | 999.99 | 999.99 | 0.022688 | 0.026516 | 0.026771 | 999.99 | 12 | 0 | 0.030167 | 999.99 | 999.99 | 0.73885 | 0.77407 | 0.77954 | 999.99 | 8 | 0.73885 | 0.74
23 | Mar | 999.99 | 999.99 | 0.026241 | 0.028969 | 0.026182 | 999.99 | 12 | 0 | 0.029833 | 999.99 | 999.99 | 0.76394 | 0.7995 | 0.79603 | 999.99 | 8 | 0.76394 | 0.76
24 | Mar | 999.99 | 999.99 | 0.023866 | 0.02787 | 999.99 | 999.99 | 12 | 0 | 0.028027 | 999.99 | 999.99 | 0.76341 | 0.7773 | 999.99 | 999.99 | 8 | 0.76341 | 0.76
25 | Mar | 999.99 | 999.99 | 0.026261 | 0.026967 | 0.026928 | 999.99 | 8 | 0 | 0.02734 | 999.99 | 999.99 | 0.73697 | 0.7604 | 0.77118 | 999.99 | 8 | 0.73697 | 0.74
26 | Mar | 999.99 | 999.99 | 0.023512 | 0.024082 | 0.27795 | 999.99 | 16 | 0 | 0.27995 | 999.99 | 999.99 | 0.73184 | 0.75098 | 0.77147 | 999.99 | 8 | 0.73184 | 0.73
27 | Mar | 999.99 | 999.99 | 0.16871 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.17481 | 999.99 | 999.99 | 0.72919 | 999.99 | 999.99 | 999.99 | 8 | 0.72919 | 0.73
28 | Mar | 999.99 | 999.99 | 0.10829 | 0.10138 | 0.099811 | 0.098123 | 8 | 0 | 0.10943 | 999.99 | 999.99 | 0.73891 | 0.76017 | 0.77336 | 0.77065 | 8 | 0.73891 | 0.74
29 | Mar | 999.99 | 999.99 | 999.99 | 0.089192 | 0.077748 | 999.99 | 12 | 0 | 0.089192 | 999.99 | 999.99 | 999.99 | 0.76211 | 0.78366 | 999.99 | 12 | 0.76211 | 0.76
30 | Mar | 999.99 | 999.99 | 0.067874 | 999.99 | 999.99 | 0.060513 | 8 | 0 | 0.067874 | 999.99 | 999.99 | 0.76064 | 999.99 | 999.99 | 0.75457 | 20 | 0.75457 | 0.75
31 | Mar | 999.99 | 999.99 | 0.071584 | 0.059728 | 0.057687 | 999.99 | 8 | 0 | 0.07182 | 999.99 | 999.99 | 0.75192 | 0.77448 | 0.78166 | 999.99 | 8 | 0.75192 | 0.75