## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Apr_23
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
2 | OFF | OFF | 0.02 | 0.02 | 0.03 | OFF | 0.03
3 | OFF | OFF | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
4 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
5 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
6 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
7 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
8 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
9 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
10 | OFF | OFF | 0.02 | 0.02 | 0.021 | OFF | 0.021
11 | OFF | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02
12 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
13 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
14 | OFF | 0.02 | 0.02 | 0.02 | OFF | OFF | 0.02
15 | OFF | 0.02 | 0.02 | 0.02 | OFF | OFF | 0.02
16 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
17 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
18 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
19 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
20 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
21 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
22 | OFF | OFF | OFF | 0.04 | 0.02 | 0.02 | 0.04
23 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
24 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
25 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
26 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
27 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
28 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
29 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
30 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:5/1/2023
[5 empty] | PHONE #: (541) 336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Apr_23 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 12:00 | 0.78 | 111 | 86.58 | 8.5 | 7.63 | 25.9417 | YES | 780
2 / 8:00 | 0.76 | 111 | 84.36 | 8.5 | 7.88 | 28.3093 | YES | 838
3 / 8:00 | 0.75 | 111 | 83.25 | 8.6 | 7.72 | 26.5194 | YES | 825
4 / 20:00 | 0.79 | 111 | 87.69 | 8.5 | 7.64 | 26.0644 | YES | 800
5 / 16:00 | 0.77 | 111 | 85.47 | 8.5 | 7.6 | 25.6359 | YES | 834
6 / 8:00 | 0.74 | 111 | 82.14 | 8.6 | 7.64 | 25.7422 | YES | 824
7 / 8:00 | 0.71 | 111 | 78.81 | 8.8 | 7.45 | 23.6602 | YES | 767
8 / 12:00 | 0.71 | 111 | 78.81 | 8.9 | 7.53 | 24.1795 | YES | 805
9 / 8:00 | 0.72 | 111 | 79.92 | 9 | 7.54 | 24.1319 | YES | 800
10 / 8:00 | 0.72 | 111 | 79.92 | 9.1 | 7.55 | 24.057 | YES | 786
11 / 8:00 | 0.73 | 111 | 81.03 | 9.1 | 7.59 | 24.4288 | YES | 792
12 / 8:00 | 0.73 | 111 | 81.03 | 9 | 7.57 | 24.4181 | YES | 810
13 / 8:00 | 0.71 | 111 | 78.81 | 9.1 | 7.5 | 23.6075 | YES | 804
14 / 4:00 | 0.71 | 111 | 78.81 | 9.2 | 7.43 | 22.8782 | YES | 832
15 / 4:00 | 0.7 | 111 | 77.7 | 9.2 | 7.41 | 22.6916 | YES | 817
16 / 12:00 | 0.72 | 111 | 79.92 | 9.3 | 7.42 | 22.6729 | YES | 825
17 / 8:00 | 0.72 | 111 | 79.92 | 9.3 | 7.41 | 22.5931 | YES | 763
18 / 8:00 | 0.71 | 111 | 78.81 | 9.1 | 7.41 | 22.8682 | YES | 775
19 / 8:00 | 0.72 | 111 | 79.92 | 8.9 | 7.41 | 23.1997 | YES | 759
20 / 8:00 | 0.72 | 111 | 79.92 | 9 | 7.45 | 23.3746 | YES | 787
21 / 8:00 | 0.73 | 111 | 81.03 | 9.1 | 7.52 | 23.8295 | YES | 804
22 / 12:00 | 0.72 | 111 | 79.92 | 9.5 | 7.47 | 22.7728 | YES | 826
23 / 12:00 | 0.72 | 111 | 79.92 | 9.7 | 7.52 | 22.8732 | YES | 808
24 / 8:00 | 0.72 | 111 | 79.92 | 9.6 | 7.57 | 23.4359 | YES | 824
25 / 8:00 | 0.72 | 111 | 79.92 | 9.6 | 7.52 | 23.0253 | YES | 837
26 / 20:00 | 0.72 | 111 | 79.92 | 9.8 | 7.47 | 22.3254 | YES | 819
27 / 8:00 | 0.7 | 111 | 77.7 | 10 | 7.48 | 22.0602 | YES | 806
28 / 8:00 | 0.71 | 111 | 78.81 | 10.3 | 7.41 | 21.1279 | YES | 754
29 / 8:00 | 0.7 | 111 | 77.7 | 10.5 | 7.34 | 20.3264 | YES | 765
30 / 8:00 | 0.69 | 111 | 76.59 | 10.6 | 7.36 | 20.3124 | YES | 783
31 |  | 111 |  |  |  |  | NO
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Apr | 999.99 | 999.99 | 0.052681 | 0.051366 | 0.050031 | 999.99 | 8 | 0 | 0.053054 | 999.99 | 999.99 | 0.75292 | 0.78826 | 0.79768 | 999.99 | 12 | 0.75292 | 0.75
2 | Apr | 999.99 | 999.99 | 0.047951 | 0.047166 | 0.047382 | 999.99 | 8 | 0 | 0.04797 | 999.99 | 999.99 | 0.75946 | 0.78578 | 0.78643 | 999.99 | 8 | 0.75946 | 0.76
3 | Apr | 999.99 | 999.99 | 0.041512 | 999.99 | 0.042415 | 0.043122 | 20 | 0 | 0.043456 | 999.99 | 999.99 | 0.75428 | 999.99 | 0.79226 | 0.8101 | 8 | 0.75428 | 0.75
4 | Apr | 999.99 | 999.99 | 999.99 | 999.99 | 0.038313 | 0.041807 | 16 | 0 | 0.042141 | 999.99 | 999.99 | 999.99 | 999.99 | 0.80828 | 0.80157 | 20 | 0.80157 | 0.8
5 | Apr | 999.99 | 999.99 | 0.041885 | 0.040708 | 0.039314 | 999.99 | 12 | 0 | 0.043043 | 999.99 | 999.99 | 0.76729 | 0.7773 | 0.76782 | 999.99 | 16 | 0.76729 | 0.77
6 | Apr | 999.99 | 999.99 | 0.04057 | 0.039334 | 0.043377 | 999.99 | 16 | 0 | 0.043377 | 999.99 | 999.99 | 0.73614 | 0.7415 | 0.7372 | 999.99 | 8 | 0.73614 | 0.74
7 | Apr | 999.99 | 999.99 | 0.045693 | 0.046439 | 0.049501 | 999.99 | 16 | 0 | 0.050718 | 999.99 | 999.99 | 0.71553 | 0.71971 | 0.73037 | 999.99 | 8 | 0.71553 | 0.72
8 | Apr | 999.99 | 999.99 | 0.043259 | 0.044202 | 0.044987 | 999.99 | 16 | 0 | 0.047853 | 999.99 | 999.99 | 0.69445 | 0.7097 | 0.73061 | 999.99 | 12 | 0.69445 | 0.69
9 | Apr | 999.99 | 999.99 | 0.044771 | 0.04797 | 0.045615 | 999.99 | 16 | 0 | 0.049128 | 999.99 | 999.99 | 0.7107 | 0.72466 | 0.74804 | 999.99 | 8 | 0.7107 | 0.71
10 | Apr | 999.99 | 999.99 | 0.045909 | 0.049443 | 0.049148 | 999.99 | 8 | 0 | 0.049737 | 999.99 | 999.99 | 0.71429 | 0.73084 | 0.74904 | 999.99 | 8 | 0.71429 | 0.71
11 | Apr | 999.99 | 999.99 | 0.0496 | 0.049541 | 0.046616 | 999.99 | 8 | 0 | 0.049992 | 999.99 | 999.99 | 0.72548 | 0.74415 | 0.76105 | 999.99 | 8 | 0.72548 | 0.73
12 | Apr | 999.99 | 999.99 | 0.051504 | 0.049639 | 0.049462 | 999.99 | 8 | 0 | 0.051857 | 999.99 | 999.99 | 0.71736 | 0.73885 | 0.73296 | 999.99 | 8 | 0.71736 | 0.72
13 | Apr | 999.99 | 999.99 | 0.046223 | 0.049619 | 999.99 | 999.99 | 8 | 0 | 0.050071 | 999.99 | 999.99 | 0.71353 | 0.7309 | 999.99 | 999.99 | 8 | 0.71353 | 0.71
14 | Apr | 999.99 | 0.048854 | 0.046793 | 0.049501 | 999.99 | 999.99 | 12 | 0 | 0.049678 | 999.99 | 0.70016 | 0.7223 | 0.73019 | 999.99 | 999.99 | 4 | 0.70016 | 0.7
15 | Apr | 999.99 | 0.046636 | 0.047539 | 0.04638 | 999.99 | 999.99 | 4 | 0 | 0.04956 | 999.99 | 0.70181 | 0.73173 | 0.73149 | 999.99 | 999.99 | 4 | 0.70181 | 0.7
16 | Apr | 999.99 | 999.99 | 0.047833 | 0.045929 | 0.047931 | 999.99 | 12 | 0 | 0.049698 | 999.99 | 999.99 | 0.71094 | 0.73043 | 0.73944 | 999.99 | 12 | 0.72 | 0.72
17 | Apr | 999.99 | 999.99 | 0.047735 | 0.047028 | 0.046007 | 999.99 | 8 | 0 | 0.049737 | 999.99 | 999.99 | 0.70858 | 0.74032 | 0.75128 | 999.99 | 8 | 0.70858 | 0.71
18 | Apr | 999.99 | 999.99 | 0.049914 | 0.046498 | 0.049148 | 999.99 | 16 | 0 | 0.050267 | 999.99 | 999.99 | 0.71959 | 0.74244 | 0.74132 | 999.99 | 8 | 0.71959 | 0.72
19 | Apr | 999.99 | 999.99 | 0.047539 | 0.048756 | 999.99 | 0.05013 | 20 | 0 | 0.050149 | 999.99 | 999.99 | 0.72643 | 0.74362 | 999.99 | 0.7312 | 8 | 0.72643 | 0.73
20 | Apr | 999.99 | 999.99 | 0.049717 | 0.048697 | 0.050031 | 999.99 | 8 | 0 | 0.050169 | 999.99 | 999.99 | 0.72401 | 0.73279 | 0.74839 | 999.99 | 8 | 0.72401 | 0.72
21 | Apr | 999.99 | 999.99 | 0.046243 | 0.049089 | 0.046753 | 999.99 | 16 | 0 | 0.049619 | 999.99 | 999.99 | 0.73167 | 0.74097 | 0.74297 | 999.99 | 8 | 0.73167 | 0.73
22 | Apr | 999.99 | 999.99 | 999.99 | 0.045654 | 0.048422 | 0.047558 | 12 | 0 | 0.04956 | 999.99 | 999.99 | 999.99 | 0.73337 | 0.74174 | 0.73738 | 12 | 0.73337 | 0.73
23 | Apr | 999.99 | 999.99 | 999.99 | 0.048108 | 0.049187 | 999.99 | 16 | 0 | 0.049187 | 999.99 | 999.99 | 999.99 | 0.7206 | 0.7375 | 999.99 | 12 | 0.7206 | 0.72
24 | Apr | 999.99 | 999.99 | 0.046479 | 0.045203 | 0.048147 | 999.99 | 8 | 0 | 0.049305 | 999.99 | 999.99 | 0.71565 | 0.72837 | 0.74262 | 999.99 | 8 | 0.71565 | 0.72
25 | Apr | 999.99 | 999.99 | 0.047656 | 0.04903 | 0.045713 | 999.99 | 8 | 0 | 0.049639 | 999.99 | 999.99 | 0.70846 | 0.73196 | 0.74185 | 999.99 | 8 | 0.70846 | 0.71
26 | Apr | 999.99 | 999.99 | 0.046871 | 0.047951 | 999.99 | 0.048324 | 20 | 0 | 0.049462 | 999.99 | 999.99 | 0.71965 | 0.73084 | 999.99 | 0.7087 | 20 | 0.7087 | 0.71
27 | Apr | 999.99 | 999.99 | 0.045811 | 0.045595 | 0.045576 | 0.048088 | 8 | 0 | 0.04956 | 999.99 | 999.99 | 0.70552 | 0.71859 | 0.73078 | 0.72519 | 8 | 0.70552 | 0.71
28 | Apr | 999.99 | 999.99 | 0.045988 | 0.047578 | 0.046302 | 999.99 | 16 | 0 | 0.050188 | 999.99 | 999.99 | 0.70952 | 0.71323 | 0.74244 | 999.99 | 8 | 0.70952 | 0.71
29 | Apr | 999.99 | 999.99 | 0.04691 | 0.048775 | 0.045988 | 999.99 | 16 | 0 | 0.049894 | 999.99 | 999.99 | 0.70735 | 0.72607 | 0.72978 | 999.99 | 8 | 0.70735 | 0.71
30 | Apr | 999.99 | 999.99 | 0.049423 | 0.049737 | 0.049776 | 999.99 | 8 | 0 | 0.049776 | 999.99 | 999.99 | 0.68856 | 0.71235 | 0.72018 | 999.99 | 8 | 0.68856 | 0.69