## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Jul_23
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
2 | 0.02 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02
3 | OFF | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02
4 | OFF | OFF | 0.04 | 0.02 | 0.02 | 0.02 | 0.04
5 | OFF | OFF | 0.02 | OFF | OFF | 0.02 | 0.02
6 | OFF | OFF | 0.03 | 0.02 | 0.02 | OFF | 0.03
7 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
8 | OFF | OFF | 0.03 | 0.02 | OFF | OFF | 0.03
9 | 0.02 | OFF | OFF | 0.02 | OFF | OFF | 0.02
10 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
11 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
12 | OFF | OFF | 0.02 | 0.037645 | 0.027713 | OFF | 0.04
13 | OFF | OFF | 0.04 | 0.02 | 0.02 | 0.02 | 0.04
14 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
15 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
16 | 0.02 | OFF | OFF | OFF | 0.02 | OFF | 0.02
17 | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.02 | 0.03
18 | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
19 | OFF | OFF | 0.03 | 0.03 | 0.02 | 0.02 | 0.03
20 | OFF | OFF | 0.03 | 0.02 | 0.02 | OFF | 0.03
21 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
22 | OFF | OFF | 0.03 | 0.03 | OFF | OFF | 0.03
23 | 0.03 | OFF | OFF | 0.03 | OFF | OFF | 0.03
24 | OFF | 0.03 | OFF | 0.03 | 0.03 | OFF | 0.03
25 | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
26 | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
27 | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
28 | OFF | OFF | 0.07 | 0.03 | 0.03 | 0.03 | 0.07
29 | OFF | OFF | 0.03 | 0.03 | 0.02 | 0.02 | 0.03
30 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
31 | OFF | OFF | 0.03 | 0.02 | 0.02 | OFF | 0.03
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:8/01/2023
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Jul_23 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 12:00 | 0.7 | 111 | 77.7 | 20.1 | 6.98 | 9.2612 | YES | 811
2 / 12:00 | 0.69 | 111 | 76.59 | 20 | 7.04 | 9.5263 | YES | 839
3 / 12:00 | 0.69 | 111 | 76.59 | 20.3 | 7.33 | 10.4097 | YES | 840
4 / 8:00 | 0.7 | 111 | 77.7 | 20.3 | 7.4 | 10.6989 | YES | 876
5 / 8:00 | 0.71 | 111 | 78.81 | 20.6 | 7.27 | 9.9966 | YES | 850
6 / 16:00 | 0.61 | 111 | 67.71 | 20.7 | 7.4 | 10.3063 | YES | 891
7 / 8:00 | 0.65 | 111 | 72.15 | 20.5 | 7.27 | 9.9949 | YES | 839
8 / 8:00 | 0.65 | 111 | 72.15 | 20.3 | 7.39 | 10.5976 | YES | 804
9 / 12:00 | 0.68 | 111 | 75.48 | 20.1 | 7.37 | 10.6983 | YES | 859
10 / 24:00 | 0.68 | 111 | 75.48 | 19.9 | 7.33 | 10.6824 | YES | 829
11 / 8:00 | 0.75 | 111 | 83.25 | 19.4 | 7.47 | 11.7366 | YES | 838
12 / 8:00 | 0.77 | 111 | 85.47 | 19.8 | 7.6 | 12.0211 | YES | 856
13 / 8:00 | 0.7 | 111 | 77.7 | 19.9 | 7.57 | 11.713 | YES | 852
14 / 8:00 | 0.68 | 111 | 75.48 | 20.1 | 7.55 | 11.444 | YES | 884
15 / 8:00 | 0.67 | 111 | 74.37 | 20.4 | 7.49 | 10.9534 | YES | 877
16 / 16:00 | 0.67 | 111 | 74.37 | 21.1 | 7.47 | 10.37 | YES | 868
17 / 8:00 | 0.66 | 111 | 73.26 | 20.8 | 7.57 | 10.9736 | YES | 829
18 / 8:00 | 0.64 | 111 | 71.04 | 20.7 | 7.6 | 11.1469 | YES | 823
19 / 8:00 | 0.68 | 111 | 75.48 | 21 | 7.64 | 11.1397 | YES | 823
20 / 8:00 | 0.71 | 111 | 78.81 | 21.2 | 7.44 | 10.2319 | YES | 827
21 / 8:00 | 0.71 | 111 | 78.81 | 21.2 | 7.49 | 10.4257 | YES | 876
22 / 8:00 | 0.7 | 111 | 77.7 | 21.3 | 7.42 | 10.0753 | YES | 849
23 / 12:00 | 0.71 | 111 | 78.81 | 21.2 | 7.38 | 10.004 | YES | 833
24 / 4:00 | 0.71 | 111 | 78.81 | 21 | 7.41 | 10.2551 | YES | 912
25 / 8:00 | 0.72 | 111 | 79.92 | 21 | 7.43 | 10.3443 | YES | 816
26 / 8:00 | 0.7 | 111 | 77.7 | 21 | 7.46 | 10.4372 | YES | 795
27 / 8:00 | 0.68 | 111 | 75.48 | 21.2 | 7.54 | 10.5864 | YES | 799
28 / 8:00 | 0.68 | 111 | 75.48 | 21.4 | 7.39 | 9.8724 | YES | 863
29 / 8:00 | 0.66 | 111 | 73.26 | 21.4 | 7.41 | 9.9239 | YES | 839
30 / 12:00 | 0.68 | 111 | 75.48 | 21.2 | 7.37 | 9.9319 | YES | 871
31 / 8:00 | 0.68 | 111 | 75.48 | 21.2 | 7.28 | 9.6014 | YES | 886
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Jul | 999.99 | 999.99 | 0.10864 | 0.031344 | 0.027556 | 999.99 | 8 | 0 | 0.11218 | 999.99 | 999.99 | 0.718 | 0.74786 | 0.74815 | 999.99 | 12 | 0.7 | 0.7
2 | Jul | 0.037076 | 999.99 | 999.99 | 0.062025 | 0.033366 | 0.02944 | 12 | 0 | 0.062025 | 0.70752 | 999.99 | 999.99 | 0.69645 | 0.7127 | 0.73838 | 12 | 0.69645 | 0.7
3 | Jul | 999.99 | 999.99 | 999.99 | 0.049109 | 0.03531 | 0.03478 | 12 | 0 | 0.053447 | 999.99 | 999.99 | 999.99 | 0.69027 | 0.70487 | 0.73284 | 12 | 0.69027 | 0.69
4 | Jul | 999.99 | 999.99 | 0.048383 | 0.032169 | 0.025201 | 0.027811 | 8 | 0 | 0.052995 | 999.99 | 999.99 | 0.69786 | 0.73832 | 0.76034 | 0.75976 | 8 | 0.69786 | 0.7
5 | Jul | 999.99 | 999.99 | 0.0591 | 999.99 | 999.99 | 0.041355 | 8 | 0 | 0.06173 | 999.99 | 999.99 | 0.72383 | 999.99 | 999.99 | 0.71583 | 8 | 0.71583 | 0.72
6 | Jul | 999.99 | 999.99 | 0.073783 | 0.035113 | 0.031384 | 999.99 | 8 | 0 | 0.073783 | 999.99 | 999.99 | 0.65759 | 0.64528 | 0.60783 | 999.99 | 16 | 0.60783 | 0.61
7 | Jul | 999.99 | 999.99 | 0.050031 | 0.034014 | 0.028361 | 0.033052 | 8 | 0 | 0.12513 | 999.99 | 999.99 | 0.6474 | 0.70552 | 0.70617 | 0.71535 | 8 | 0.6474 | 0.65
8 | Jul | 999.99 | 999.99 | 0.0803 | 0.037763 | 999.99 | 999.99 | 8 | 0 | 0.0803 | 999.99 | 999.99 | 0.65476 | 0.69993 | 999.99 | 999.99 | 8 | 0.65476 | 0.65
9 | Jul | 0.039078 | 999.99 | 999.99 | 0.051916 | 999.99 | 999.99 | 12 | 0 | 0.051916 | 0.68485 | 999.99 | 999.99 | 0.69086 | 999.99 | 999.99 | 12 | 0.69086 | 0.69
10 | Jul | 0.086443 | 999.99 | 0.062221 | 0.035722 | 0.03319 | 999.99 | 8 | 0 | 0.063811 | 0.68768 | 999.99 | 0.72107 | 0.76617 | 0.77772 | 999.99 | 24 | 0.68 | 0.68
11 | Jul | 999.99 | 999.99 | 0.048559 | 0.03421 | 0.035133 | 0.03951 | 8 | 0 | 0.05223 | 999.99 | 999.99 | 0.74533 | 0.79544 | 0.82494 | 0.82618 | 8 | 0.74533 | 0.75
12 | Jul | 999.99 | 999.99 | 0.054644 | 0.037645 | 0.027713 | 999.99 | 8 | 0 | 0.056136 | 999.99 | 999.99 | 0.76694 | 0.78714 | 0.78926 | 999.99 | 8 | 0.76694 | 0.77
13 | Jul | 999.99 | 999.99 | 0.054055 | 0.028557 | 0.034878 | 0.034956 | 8 | 0 | 0.054252 | 999.99 | 999.99 | 0.71359 | 0.73226 | 0.73608 | 0.73084 | 8 | 0.71359 | 0.71
14 | Jul | 999.99 | 999.99 | 0.087072 | 0.028263 | 0.037292 | 999.99 | 8 | 0 | 0.093157 | 999.99 | 999.99 | 0.67879 | 0.72248 | 0.73072 | 999.99 | 8 | 0.67879 | 0.68
15 | Jul | 999.99 | 999.99 | 0.14341 | 0.045281 | 999.99 | 999.99 | 8 | 0 | 0.14447 | 999.99 | 999.99 | 0.67843 | 0.70487 | 999.99 | 999.99 | 8 | 0.67843 | 0.68
16 | Jul | 0.045752 | 999.99 | 999.99 | 999.99 | 0.05541 | 999.99 | 16 | 0 | 0.05541 | 0.68579 | 999.99 | 999.99 | 999.99 | 0.67278 | 999.99 | 16 | 0.67278 | 0.67
17 | Jul | 999.99 | 999.99 | 0.064577 | 0.040452 | 0.034132 | 0.036978 | 8 | 0 | 0.064577 | 999.99 | 999.99 | 0.65906 | 0.67702 | 0.6931 | 0.69227 | 8 | 0.65906 | 0.66
18 | Jul | 999.99 | 999.99 | 0.06385 | 0.038902 | 0.034544 | 0.036605 | 8 | 0 | 0.080987 | 999.99 | 999.99 | 0.63768 | 0.67837 | 0.72401 | 0.73632 | 8 | 0.63768 | 0.64
19 | Jul | 999.99 | 999.99 | 0.046832 | 0.035486 | 0.038372 | 0.044359 | 8 | 0 | 0.047185 | 999.99 | 999.99 | 0.68008 | 0.72154 | 0.74338 | 0.74986 | 8 | 0.68008 | 0.68
20 | Jul | 999.99 | 999.99 | 0.048716 | 0.037665 | 0.039432 | 999.99 | 8 | 0 | 0.050326 | 999.99 | 999.99 | 0.71918 | 0.74774 | 0.76523 | 999.99 | 8 | 0.71918 | 0.72
21 | Jul | 999.99 | 999.99 | 0.065244 | 0.040119 | 0.035624 | 999.99 | 8 | 0 | 0.065244 | 999.99 | 999.99 | 0.71535 | 0.75457 | 0.78955 | 999.99 | 8 | 0.71535 | 0.72
22 | Jul | 999.99 | 999.99 | 0.14166 | 0.050601 | 999.99 | 999.99 | 8 | 0 | 0.14319 | 999.99 | 999.99 | 0.70093 | 0.74415 | 999.99 | 999.99 | 8 | 0.70093 | 0.7
23 | Jul | 0.055037 | 999.99 | 999.99 | 0.072801 | 999.99 | 999.99 | 12 | 0 | 0.076315 | 0.7266 | 999.99 | 999.99 | 0.71577 | 999.99 | 999.99 | 12 | 0.71577 | 0.72
24 | Jul | 999.99 | 0.083479 | 999.99 | 0.046164 | 0.046793 | 999.99 | 4 | 0 | 0.088092 | 999.99 | 0.72071 | 999.99 | 0.76164 | 0.7796 | 999.99 | 4 | 0.72071 | 0.72
25 | Jul | 999.99 | 999.99 | 0.071565 | 0.053133 | 0.046498 | 0.050915 | 8 | 0 | 0.071918 | 999.99 | 999.99 | 0.70782 | 0.73667 | 0.75487 | 0.75652 | 8 | 0.70782 | 0.71
26 | Jul | 999.99 | 999.99 | 0.079161 | 0.054605 | 0.052485 | 0.051543 | 8 | 0 | 0.083244 | 999.99 | 999.99 | 0.69745 | 0.72501 | 0.73756 | 0.74321 | 8 | 0.69745 | 0.7
27 | Jul | 999.99 | 999.99 | 0.081497 | 0.058825 | 0.060788 | 0.061554 | 8 | 0 | 0.081575 | 999.99 | 999.99 | 0.69033 | 0.72707 | 0.73496 | 0.73767 | 8 | 0.69033 | 0.69
28 | Jul | 999.99 | 999.99 | 0.098398 | 0.06334 | 0.064047 | 0.072468 | 8 | 0 | 0.098417 | 999.99 | 999.99 | 0.67631 | 0.70982 | 0.72884 | 0.73167 | 8 | 0.67631 | 0.68
29 | Jul | 999.99 | 999.99 | 0.088936 | 0.11031 | 0.11671 | 0.094786 | 16 | 0 | 0.11765 | 999.99 | 999.99 | 0.67031 | 0.6852 | 0.7226 | 0.74062 | 8 | 0.67031 | 0.67
30 | Jul | 999.99 | 999.99 | 999.99 | 0.10171 | 0.092568 | 999.99 | 12 | 0 | 0.10224 | 999.99 | 999.99 | 999.99 | 0.69056 | 0.70263 | 999.99 | 12 | 0.69056 | 0.69
31 | Jul | 999.99 | 999.99 | 0.053349 | 0.042278 | 999.99 | 999.99 | 8 | 0 | 0.055155 | 999.99 | 999.99 | 0.67578 | 0.71088 | 999.99 | 999.99 | 8 | 0.67578 | 0.68