## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Aug_23
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.02 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
2 | OFF | 0.02 | 0.02 | 0.02 | 0.034407 | OFF | 0.03
3 | OFF | 0.03 | 0.03 | OFF | 0.03 | 0.03 | 0.03
4 | OFF | OFF | OFF | 0.03 | 0.03 | OFF | 0.03
5 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
6 | OFF | OFF | 0.03 | 0.03 | OFF | OFF | 0.03
7 | OFF | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.04
8 | OFF | OFF | 0.03 | 0.03 | OFF | 0.03 | 0.03
9 | OFF | OFF | 0.03 | 0.03 | 0.02 | OFF | 0.03
10 | OFF | OFF | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
11 | OFF | OFF | 0.03 | 0.04 | 0.03 | OFF | 0.04
12 | OFF | OFF | 0.04 | 0.03 | 0.03 | OFF | 0.04
13 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
14 | OFF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
15 | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
16 | OFF | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.03
17 | OFF | OFF | 0.04 | 0.03 | 0.03 | OFF | 0.04
18 | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
19 | OFF | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.03
20 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
21 | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
22 | OFF | OFF | OFF | 0.04 | OFF | OFF | 0.04
23 | 0.03 | OFF | 0.03 | 0.04 | 0.03 | OFF | 0.04
24 | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
25 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
26 | OFF | OFF | 0.03 | 0.04 | 0.03 | OFF | 0.04
27 | OFF | OFF | 0.03 | 0.04 | 0.03 | OFF | 0.04
28 | OFF | OFF | 0.03 | 0.04 | 0.03 | OFF | 0.04
29 | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
30 | OFF | OFF | OFF | 0.03 | 0.03 | OFF | 0.03
31 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:09/01/2023
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Aug_23 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 24:00 | 0.67 | 111 | 74.37 | 21.1 | 7.55 | 10.6858 | YES | 874
2 / 4:00 | 0.69 | 111 | 76.59 | 20.8 | 7.45 | 10.5274 | YES | 840
3 / 4:00 | 0.7 | 111 | 77.7 | 21 | 7.22 | 9.5371 | YES | 831
4 / 12:00 | 0.75 | 111 | 83.25 | 21 | 7.2 | 9.5205 | YES | 844
5 / 8:00 | 0.68 | 111 | 75.48 | 21.3 | 7.18 | 9.1839 | YES | 814
6 / 8:00 | 0.68 | 111 | 75.48 | 21.4 | 7.22 | 9.2604 | YES | 819
7 / 4:00 | 0.68 | 111 | 75.48 | 21.5 | 7.28 | 9.4081 | YES | 877
8 / 8:00 | 0.69 | 111 | 76.59 | 21.6 | 7.41 | 9.8245 | YES | 823
9 / 8:00 | 0.72 | 111 | 79.92 | 21.8 | 7.4 | 9.6895 | YES | 858
10 / 8:00 | 0.73 | 111 | 81.03 | 21.9 | 7.43 | 9.7445 | YES | 842
11 / 8:00 | 0.72 | 111 | 79.92 | 21.8 | 7.17 | 8.8849 | YES | 820
12 / 8:00 | 0.72 | 111 | 79.92 | 21.7 | 7.26 | 9.2544 | YES | 838
13 / 8:00 | 0.72 | 111 | 79.92 | 21.7 | 7.29 | 9.3596 | YES | 808
14 / 4:00 | 0.75 | 111 | 83.25 | 21.9 | 7.36 | 9.5132 | YES | 838
15 / 8:00 | 0.73 | 111 | 81.03 | 22.3 | 7.4 | 9.3774 | YES | 852
16 / 12:00 | 0.72 | 111 | 79.92 | 22.7 | 7.43 | 9.2194 | YES | 863
17 / 8:00 | 0.72 | 111 | 79.92 | 23.2 | 7.38 | 8.7448 | YES | 850
18 / 8:00 | 0.7 | 111 | 77.7 | 23.3 | 7.35 | 8.5676 | YES | 889
19 / 12:00 | 0.71 | 111 | 78.81 | 22.9 | 7.11 | 8.0489 | YES | 809
20 / 8:00 | 0.69 | 111 | 76.59 | 22.6 | 7.21 | 8.5126 | YES | 829
21 / 8:00 | 0.73 | 111 | 81.03 | 22.1 | 7.12 | 8.5524 | YES | 843
22 / 12:00 | 0.77 | 111 | 85.47 | 21.4 | 7.48 | 10.3185 | YES | 838
23 / 800 | 0.71 | 111 | 78.81 | 20.9 | 7.37 | 10.1707 | YES | 902
24 / 8:00 | 0.69 | 111 | 76.59 | 20.8 | 7.2 | 9.5837 | YES | 857
25 / 8:00 | 0.7 | 111 | 77.7 | 20.9 | 7.12 | 9.2471 | YES | 881
26 / 8:00 | 0.69 | 111 | 76.59 | 20.7 | 7.32 | 10.0941 | YES | 888
27 / 8:00 | 0.7 | 111 | 77.7 | 20.6 | 7.2 | 9.7257 | YES | 834
28 / 8:00 | 0.71 | 111 | 78.81 | 20.3 | 7.48 | 11.037 | YES | 814
29 / 8:00 | 0.71 | 111 | 78.81 | 20.1 | 7.37 | 10.7354 | YES | 830
30 / 12:00 | 0.74 | 111 | 82.14 | 20 | 7.34 | 10.7242 | YES | 829
31 / 8:00 | 0.68 | 111 | 75.48 | 19.7 | 7.41 | 11.1567 | YES | 835
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Aug | 0.04746 | 999.99 | 999.99 | 0.043573 | 0.036173 | 999.99 | 0 | 0 | 0.04797 | 0.65918 | 999.99 | 999.99 | 0.71406 | 0.72743 | 999.99 | 24 | 0.67 | 0.67
2 | Aug | 999.99 | 0.12715 | 0.045006 | 0.034524 | 0.034407 | 999.99 | 4 | 0 | 0.12725 | 999.99 | 0.67584 | 0.71453 | 0.75716 | 0.75711 | 999.99 | 4 | 0.67584 | 0.68
3 | Aug | 999.99 | 0.06226 | 0.040629 | 999.99 | 0.037626 | 0.041453 | 4 | 0 | 0.065048 | 999.99 | 0.7074 | 0.78431 | 999.99 | 0.79197 | 0.81063 | 4 | 0.7074 | 0.71
4 | Aug | 999.99 | 999.99 | 999.99 | 0.043279 | 0.037744 | 999.99 | 12 | 0 | 0.043279 | 999.99 | 999.99 | 999.99 | 0.74933 | 0.77136 | 999.99 | 12 | 0.74933 | 0.75
5 | Aug | 999.99 | 999.99 | 0.088132 | 0.038352 | 0.041395 | 999.99 | 8 | 0 | 0.090546 | 999.99 | 999.99 | 0.67649 | 0.73267 | 0.74639 | 999.99 | 8 | 0.67649 | 0.68
6 | Aug | 999.99 | 999.99 | 0.04377 | 0.037606 | 999.99 | 999.99 | 8 | 0 | 0.046577 | 999.99 | 999.99 | 0.69486 | 0.73856 | 999.99 | 999.99 | 8 | 0.69486 | 0.69
7 | Aug | 999.99 | 0.048756 | 999.99 | 0.045517 | 0.041885 | 0.040197 | 4 | 0 | 0.050934 | 999.99 | 0.68173 | 999.99 | 0.70458 | 0.73373 | 0.74162 | 4 | 0.68173 | 0.68
8 | Aug | 999.99 | 999.99 | 0.058845 | 0.049266 | 999.99 | 0.045792 | 8 | 0 | 0.062457 | 999.99 | 999.99 | 0.68668 | 0.72301 | 999.99 | 0.70505 | 8 | 0.68668 | 0.69
9 | Aug | 999.99 | 999.99 | 0.048029 | 0.040786 | 0.046439 | 999.99 | 8 | 0 | 0.048029 | 999.99 | 999.99 | 0.71318 | 0.75222 | 0.76688 | 999.99 | 8 | 0.71318 | 0.71
10 | Aug | 999.99 | 999.99 | 0.074293 | 0.042396 | 0.043613 | 0.048284 | 8 | 0 | 0.25105 | 999.99 | 999.99 | 0.72495 | 0.7723 | 0.75811 | 0.78985 | 8 | 0.72495 | 0.72
11 | Aug | 999.99 | 999.99 | 0.068581 | 0.049619 | 0.046577 | 999.99 | 8 | 0 | 0.074077 | 999.99 | 999.99 | 0.71294 | 0.75398 | 0.78107 | 999.99 | 8 | 0.71294 | 0.71
12 | Aug | 999.99 | 999.99 | 0.10009 | 0.050031 | 0.05278 | 999.99 | 8 | 0 | 0.10429 | 999.99 | 999.99 | 0.72507 | 0.76806 | 0.7879 | 999.99 | 8 | 0.72507 | 0.73
13 | Aug | 999.99 | 999.99 | 0.11748 | 0.055115 | 0.067737 | 999.99 | 8 | 0 | 0.11748 | 999.99 | 999.99 | 0.72177 | 0.78272 | 0.79544 | 999.99 | 8 | 0.72177 | 0.72
14 | Aug | 999.99 | 0.099791 | 0.075647 | 0.063948 | 0.069504 | 0.070642 | 4 | 0 | 0.10548 | 999.99 | 0.74386 | 0.77442 | 0.80663 | 0.79303 | 0.79373 | 4 | 0.74386 | 0.74
15 | Aug | 999.99 | 999.99 | 0.084971 | 0.073822 | 0.075039 | 0.073253 | 8 | 0 | 0.085148 | 999.99 | 999.99 | 0.73273 | 0.76947 | 0.76388 | 0.77077 | 8 | 0.73273 | 0.73
16 | Aug | 999.99 | 999.99 | 999.99 | 0.093431 | 0.084755 | 0.084736 | 12 | 0 | 0.09351 | 999.99 | 999.99 | 999.99 | 0.71406 | 0.74686 | 0.76935 | 12 | 0.71406 | 0.71
17 | Aug | 999.99 | 999.99 | 0.1249 | 0.10603 | 0.096219 | 999.99 | 8 | 0 | 0.13194 | 999.99 | 999.99 | 0.72754 | 0.75404 | 0.771 | 999.99 | 8 | 0.72754 | 0.73
18 | Aug | 999.99 | 999.99 | 0.18537 | 0.13055 | 0.1139 | 0.11357 | 8 | 0 | 0.18781 | 999.99 | 999.99 | 0.70334 | 0.70958 | 0.73155 | 0.76447 | 8 | 0.70334 | 0.7
19 | Aug | 999.99 | 999.99 | 999.99 | 0.17587 | 0.13387 | 0.13628 | 12 | 0 | 0.17587 | 999.99 | 999.99 | 999.99 | 0.72389 | 0.7574 | 0.76517 | 12 | 0.72389 | 0.72
20 | Aug | 999.99 | 999.99 | 0.2085 | 0.15992 | 0.1554 | 999.99 | 8 | 0 | 0.20969 | 999.99 | 999.99 | 0.68397 | 0.75045 | 0.77047 | 999.99 | 8 | 0.68397 | 0.68
21 | Aug | 999.99 | 999.99 | 0.17742 | 0.052053 | 0.042337 | 0.044418 | 8 | 0 | 0.18027 | 999.99 | 999.99 | 0.73208 | 0.77489 | 0.79256 | 0.7965 | 8 | 0.73208 | 0.73
22 | Aug | 999.99 | 999.99 | 999.99 | 0.046106 | 999.99 | 999.99 | 12 | 0 | 0.046106 | 999.99 | 999.99 | 999.99 | 0.76223 | 999.99 | 999.99 | 12 | 0.76223 | 0.76
23 | Aug | 0.063948 | 999.99 | 0.064793 | 0.045634 | 0.046498 | 999.99 | 8 | 0 | 0.068267 | 0.74168 | 999.99 | 0.71577 | -0.74641 | 0.75917 | 999.99 | 8 | -0.74641 | -0.75
24 | Aug | 999.99 | 999.99 | 0.09777 | 0.048363 | 0.044319 | 0.044182 | 8 | 0 | 0.098908 | 999.99 | 999.99 | 0.69751 | 0.74127 | 0.77253 | 0.77465 | 8 | 0.69751 | 0.7
25 | Aug | 999.99 | 999.99 | 0.077787 | 0.047637 | 0.04746 | 999.99 | 8 | 0 | 0.080064 | 999.99 | 999.99 | 0.69875 | 0.74639 | 0.7703 | 999.99 | 8 | 0.69875 | 0.7
26 | Aug | 999.99 | 999.99 | 0.1301 | 0.049619 | 0.051523 | 999.99 | 8 | 0 | 0.13681 | 999.99 | 999.99 | 0.70634 | 0.74291 | 0.76924 | 999.99 | 8 | 0.70634 | 0.71
27 | Aug | 999.99 | 999.99 | 0.083774 | 0.052603 | 0.045477 | 999.99 | 8 | 0 | 0.083774 | 999.99 | 999.99 | 0.71094 | 0.74745 | 0.76329 | 999.99 | 8 | 0.71094 | 0.71
28 | Aug | 999.99 | 999.99 | 0.085855 | 0.047205 | 0.048932 | 999.99 | 8 | 0 | 0.085874 | 999.99 | 999.99 | 0.71465 | 0.75169 | 0.78031 | 999.99 | 8 | 0.71465 | 0.71
29 | Aug | 999.99 | 999.99 | 0.10397 | 0.05062 | 0.045556 | 0.048775 | 8 | 0 | 0.10397 | 999.99 | 999.99 | 0.69669 | 0.74992 | 0.77424 | 0.77689 | 8 | 0.69669 | 0.7
30 | Aug | 999.99 | 999.99 | 999.99 | 0.05331 | 0.048756 | 999.99 | 12 | 0 | 0.053388 | 999.99 | 999.99 | 999.99 | 0.73685 | 0.75128 | 999.99 | 12 | 0.73685 | 0.74
31 | Aug | 999.99 | 999.99 | 0.069386 | 0.049796 | 0.054252 | 999.99 | 8 | 0 | 0.073135 | 999.99 | 999.99 | 0.68544 | 0.72725 | 0.74533 | 999.99 | 8 | 0.68544 | 0.69