## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Oct_23
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
2 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
3 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
4 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
5 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
6 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
7 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
8 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
9 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
10 | OFF | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02
11 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
12 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
13 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
14 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
15 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
16 | OFF | OFF | 0.01 | 0.03 | OFF | OFF | 0.03
17 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
18 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
19 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
20 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
21 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
22 | OFF | OFF | OFF | 0.03 | OFF | OFF | 0.03
23 | OFF | OFF | 0.02 | 0.01 | 0.01 | OFF | 0.02
24 | OFF | OFF | OFF | 0.01 | 0.01 | OFF | 0.01
25 | OFF | OFF | OFF | 0.01 | 0.01 | OFF | 0.01
26 | OFF | OFF | 0.02 | 0.01 | 0.01 | OFF | 0.02
27 | OFF | OFF | 0.01 | 0.02 | OFF | OFF | 0.02
28 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
29 | OFF | OFF | 0.02 | 0.02 | 0.10217 | OFF | 0.02
30 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
31 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:11/01/2023
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Oct_23 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 12:00 | 0.69 | 111 | 76.59 | 15.7 | 7.14 | 13.2128 | YES | 841
2 / 8:00 | 0.63 | 111 | 69.93 | 15.5 | 7.06 | 12.9092 | YES | 817
3 / 8:00 | 0.68 | 111 | 75.48 | 15.4 | 7.26 | 14.0798 | YES | 831
4 / 8:00 | 0.73 | 111 | 81.03 | 15.2 | 7.3 | 14.5657 | YES | 859
5 / 8:00 | 0.77 | 111 | 85.47 | 15.3 | 7.31 | 14.589 | YES | 892
6 / 8:00 | 0.75 | 111 | 83.25 | 15.6 | 7.32 | 14.3198 | YES | 856
7 / 8:00 | 0.69 | 111 | 76.59 | 15.7 | 7.34 | 14.2326 | YES | 879
8 / 8:00 | 0.66 | 111 | 73.26 | 15.8 | 7.38 | 14.3002 | YES | 851
9 / 8:00 | 0.65 | 111 | 72.15 | 15.8 | 7.26 | 13.6611 | YES | 885
10 / 8:00 | 0.68 | 111 | 75.48 | 15.8 | 7.31 | 13.9651 | YES | 991
11 / 12:00 | 0.74 | 111 | 82.14 | 15.2 | 7.47 | 15.5312 | YES | 1009
12 / 8:00 | 0.74 | 111 | 82.14 | 15.2 | 7.48 | 15.5888 | YES | 837
13 / 8:00 | 0.79 | 111 | 87.69 | 15.1 | 7.43 | 15.4931 | YES | 1023
14 / 12:00 | 0.73 | 111 | 81.03 | 15.2 | 7.48 | 15.5711 | YES | 989
15 / 8:00 | 0.63 | 111 | 69.93 | 14.7 | 7.41 | 15.5093 | YES | 1002
16 / 8:00 | 0.63 | 111 | 69.93 | 14.5 | 7.31 | 15.1459 | YES | 1039
17 / 8:00 | 0.68 | 111 | 75.48 | 14.2 | 7.33 | 15.656 | YES | 1047
18 / 8:00 | 0.74 | 111 | 82.14 | 14.2 | 7.35 | 15.8805 | YES | 883
19 / 8:00 | 0.77 | 111 | 85.47 | 14.1 | 7.35 | 16.0414 | YES | 888
20 / 12:00 | 0.77 | 111 | 85.47 | 14.2 | 7.39 | 16.1725 | YES | 877
21 / 12:00 | 0.79 | 111 | 87.69 | 14.2 | 7.39 | 16.2094 | YES | 872
22 / 12:00 | 0.77 | 111 | 85.47 | 14.1 | 7.45 | 16.6461 | YES | 878
23 / 8:00 | 0.74 | 111 | 82.14 | 13.9 | 7.42 | 16.6263 | YES | 832
24 / 12:00 | 0.75 | 111 | 83.25 | 14 | 7.49 | 16.9683 | YES | 862
25 / 12:00 | 0.75 | 111 | 83.25 | 13.6 | 7.56 | 17.8825 | YES | 857
26 / 8:00 | 0.72 | 111 | 79.92 | 13.5 | 7.6 | 18.2074 | YES | 846
27 / 8:00 | 0.73 | 111 | 81.03 | 13.4 | 7.62 | 18.4855 | YES | 834
28 / 4:00 | 0.71 | 111 | 78.81 | 13 | 7.52 | 18.2542 | YES | 900
29 / 8:00 | 0.69 | 111 | 76.59 | 12.3 | 7.57 | 19.557 | YES | 858
30 / 12:00 | 0.75 | 111 | 83.25 | 11.6 | 7.6 | 20.8264 | YES | 898
31 / 12:00 | 0.79 | 111 | 87.69 | 11.2 | 7.55 | 21.1044 | YES | 862
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Oct | 999.99 | 999.99 | 999.99 | 0.048736 | 999.99 | 999.99 | 12 | 0 | 0.048736 | 999.99 | 999.99 | 999.99 | 0.69551 | 999.99 | 999.99 | 12 | 0.69551 | 0.7
2 | Oct | 999.99 | 999.99 | 0.093373 | 0.03849 | 999.99 | 999.99 | 8 | 0 | 0.097593 | 999.99 | 999.99 | 0.63203 | 0.7342 | 999.99 | 999.99 | 8 | 0.63203 | 0.63
3 | Oct | 999.99 | 999.99 | 0.08662 | 0.039824 | 0.033621 | 999.99 | 8 | 0 | 0.088033 | 999.99 | 999.99 | 0.68644 | 0.7481 | 0.8028 | 999.99 | 8 | 0.68644 | 0.69
4 | Oct | 999.99 | 999.99 | 0.061259 | 0.032915 | 0.041316 | 999.99 | 8 | 0 | 0.063674 | 999.99 | 999.99 | 0.72513 | 0.80645 | 0.83337 | 999.99 | 8 | 0.72513 | 0.73
5 | Oct | 999.99 | 999.99 | 0.08662 | 0.033857 | 999.99 | 999.99 | 8 | 0 | 0.087935 | 999.99 | 999.99 | 0.77212 | 0.82724 | 999.99 | 999.99 | 8 | 0.77212 | 0.77
6 | Oct | 999.99 | 999.99 | 0.10648 | 0.040649 | 0.041179 | 999.99 | 8 | 0 | 0.10735 | 999.99 | 999.99 | 0.76123 | 0.78119 | 0.78372 | 999.99 | 8 | 0.76123 | 0.76
7 | Oct | 999.99 | 999.99 | 0.11907 | 0.044947 | 0.04956 | 999.99 | 8 | 0 | 0.12162 | 999.99 | 999.99 | 0.69881 | 0.72542 | 0.73455 | 999.99 | 8 | 0.69881 | 0.7
8 | Oct | 999.99 | 999.99 | 0.13084 | 0.035624 | 0.042239 | 999.99 | 8 | 0 | 0.13084 | 999.99 | 999.99 | 0.66489 | 0.69651 | 0.71818 | 999.99 | 8 | 0.66489 | 0.66
9 | Oct | 999.99 | 999.99 | 0.12727 | 0.039922 | 0.035153 | 999.99 | 8 | 0 | 0.13334 | 999.99 | 999.99 | 0.64864 | 0.69922 | 0.74474 | 999.99 | 8 | 0.64864 | 0.65
10 | Oct | 999.99 | 999.99 | 0.070838 | 0.050345 | 0.032267 | 0.034524 | 8 | 0 | 0.072919 | 999.99 | 999.99 | 0.67996 | 0.72101 | 0.78131 | 0.80533 | 8 | 0.67996 | 0.68
11 | Oct | 999.99 | 999.99 | 999.99 | 0.042553 | 0.039844 | 999.99 | 12 | 0 | 0.046498 | 999.99 | 999.99 | 999.99 | 0.7382 | 0.77242 | 999.99 | 12 | 0.7382 | 0.74
12 | Oct | 999.99 | 999.99 | 0.090369 | 0.044457 | 999.99 | 999.99 | 8 | 0 | 0.093314 | 999.99 | 999.99 | 0.74886 | 0.80345 | 999.99 | 999.99 | 8 | 0.74886 | 0.75
13 | Oct | 999.99 | 999.99 | 0.097397 | 0.042886 | 0.04905 | 999.99 | 8 | 0 | 0.097397 | 999.99 | 999.99 | 0.78667 | 0.84555 | 0.82789 | 999.99 | 8 | 0.78667 | 0.79
14 | Oct | 999.99 | 999.99 | 0.051523 | 0.051013 | 999.99 | 999.99 | 12 | 0 | 0.054487 | 999.99 | 999.99 | 0.74221 | 0.74056 | 999.99 | 999.99 | 12 | 0.74056 | 0.74
15 | Oct | 999.99 | 999.99 | 0.091253 | 0.049501 | 999.99 | 999.99 | 8 | 0 | 0.093353 | 999.99 | 999.99 | 0.63462 | 0.69433 | 999.99 | 999.99 | 8 | 0.63462 | 0.63
16 | Oct | 999.99 | 999.99 | 0.083479 | 0.06014 | 999.99 | 999.99 | 8 | 0 | 0.083479 | 999.99 | 999.99 | 0.63226 | 0.70022 | 999.99 | 999.99 | 8 | 0.63226 | 0.63
17 | Oct | 999.99 | 999.99 | 0.097338 | 0.055783 | 0.054507 | 999.99 | 8 | 0 | 0.099438 | 999.99 | 999.99 | 0.6812 | 0.75292 | 0.78678 | 999.99 | 8 | 0.6812 | 0.68
18 | Oct | 999.99 | 999.99 | 0.097397 | 0.061809 | 0.063693 | 999.99 | 8 | 0 | 0.097397 | 999.99 | 999.99 | 0.74592 | 0.81582 | 0.84049 | 999.99 | 8 | 0.74592 | 0.75
19 | Oct | 999.99 | 999.99 | 0.18781 | 0.076806 | 0.067285 | 999.99 | 8 | 0 | 0.18781 | 999.99 | 999.99 | 0.77707 | 0.81364 | 0.83154 | 999.99 | 8 | 0.77707 | 0.78
20 | Oct | 999.99 | 999.99 | 999.99 | 0.089074 | 0.075235 | 999.99 | 12 | 0 | 0.089152 | 999.99 | 999.99 | 999.99 | 0.77595 | 0.81187 | 999.99 | 12 | 0.77595 | 0.78
21 | Oct | 999.99 | 999.99 | 999.99 | 0.088132 | 999.99 | 999.99 | 12 | 0 | 0.089035 | 999.99 | 999.99 | 999.99 | 0.79468 | 999.99 | 999.99 | 12 | 0.79468 | 0.79
22 | Oct | 999.99 | 999.99 | 0.1894 | 0.088426 | 999.99 | 999.99 | 8 | 0 | 0.1894 | 999.99 | 999.99 | 0.74609 | 0.77607 | 999.99 | 999.99 | 8 | 0.74609 | 0.75
23 | Oct | 999.99 | 999.99 | 0.14682 | 0.1045 | 0.092882 | 999.99 | 8 | 0 | 0.15232 | 999.99 | 999.99 | 0.7405 | 0.74645 | 0.77589 | 999.99 | 8 | 0.7405 | 0.74
24 | Oct | 999.99 | 999.99 | 999.99 | 0.11402 | 0.1033 | 999.99 | 12 | 0 | 0.1171 | 999.99 | 999.99 | 999.99 | 0.74439 | 0.77112 | 999.99 | 12 | 0.74439 | 0.74
25 | Oct | 999.99 | 999.99 | 999.99 | 0.062339 | 0.062633 | 999.99 | 16 | 0 | 0.065185 | 999.99 | 999.99 | 999.99 | 0.7372 | 0.75799 | 999.99 | 12 | 0.7372 | 0.74
26 | Oct | 999.99 | 999.99 | 0.10317 | 0.063556 | 0.063517 | 999.99 | 8 | 0 | 0.10319 | 999.99 | 999.99 | 0.71382 | 0.74768 | 0.77006 | 999.99 | 8 | 0.71382 | 0.71
27 | Oct | 999.99 | 999.99 | 0.11347 | 0.074548 | 999.99 | 999.99 | 8 | 0 | 0.11622 | 999.99 | 999.99 | 0.72348 | 0.75369 | 999.99 | 999.99 | 8 | 0.72348 | 0.72
28 | Oct | 999.99 | 0.081281 | 0.077532 | 0.075824 | 0.073527 | 999.99 | 4 | 0 | 0.081281 | 999.99 | 0.71665 | 0.73314 | 0.7478 | 0.75398 | 999.99 | 4 | 0.71665 | 0.72
29 | Oct | 999.99 | 999.99 | 0.12988 | 0.075196 | 0.10217 | 999.99 | 8 | 0 | 0.12992 | 999.99 | 999.99 | 0.68697 | 0.75257 | 0.7773 | 999.99 | 8 | 0.68697 | 0.69
30 | Oct | 999.99 | 999.99 | 999.99 | 0.095041 | 0.092195 | 999.99 | 16 | 0 | 0.095826 | 999.99 | 999.99 | 999.99 | 0.75658 | 0.7965 | 999.99 | 12 | 0.75658 | 0.76
31 | Oct | 999.99 | 999.99 | 999.99 | 0.096022 | 0.099163 | 999.99 | 16 | 0 | 0.09985 | 999.99 | 999.99 | 999.99 | 0.79338 | 0.81829 | 999.99 | 12 | 0.79338 | 0.79