## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Nov_23
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
2 | OFF | OFF | OFF | 0.02 | 0.03 | OFF | 0.03
3 | OFF | OFF | 0.02 | 0.02 | 0.01 | OFF | 0.02
4 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
5 | OFF | OFF | OFF | 0.02 | 0.03 | OFF | 0.03
6 | OFF | OFF | 0.02 | 0.04 | 0.02 | OFF | 0.04
7 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
8 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
9 | OFF | OFF | 0.02 | 0.02 | 0.01 | OFF | 0.02
10 | OFF | OFF | OFF | 0.01 | OFF | OFF | 0.01
11 | OFF | OFF | 0.01 | 0.01 | OFF | OFF | 0.01
12 | OFF | OFF | OFF | 0.01 | 0.01 | OFF | 0.01
13 | OFF | OFF | 0.01 | 0.01 | OFF | OFF | 0.01
14 | OFF | OFF | 0.01 | 0.03 | 0.02 | OFF | 0.03
15 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
16 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
17 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
18 | OFF | OFF | 0.02 | 0.01 | OFF | 0.02 | 0.02
19 | OFF | OFF | 0.01 | 0.01 | 0.01 | OFF | 0.01
20 | OFF | OFF | 0.01 | 0.01 | 0.01 | OFF | 0.01
21 | OFF | OFF | 0.01 | 0.01 | OFF | OFF | 0.01
22 | OFF | OFF | 0.01 | 0.01 | OFF | OFF | 0.01
23 | OFF | OFF | 0.01 | 0.02 | 0.02 | OFF | 0.02
24 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
25 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
26 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
27 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
28 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
29 | OFF | OFF | 0.02 | 0.02 | 0.01 | OFF | 0.02
30 | OFF | OFF | 0.01 | 0.01 | 0.01 | OFF | 0.01
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:12/01/23
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Nov_23 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 12:00 | 0.8 | 111 | 88.8 | 10.7 | 7.52 | 21.606 | YES | 868
2 / 12:00 | 0.81 | 111 | 89.91 | 10.7 | 7.78 | 23.707 | YES | 861
3 / 8:00 | 0.79 | 111 | 87.69 | 10.7 | 7.78 | 23.6531 | YES | 830
4 / 12:00 | 0.71 | 111 | 78.81 | 10.9 | 7.6 | 21.709 | YES | 832
5 / 12:00 | 0.65 | 111 | 72.15 | 11.2 | 7.43 | 19.9242 | YES | 868
6 / 8:00 | 0.64 | 111 | 71.04 | 11.5 | 7.37 | 19.1154 | YES | 886
7 / 8:00 | 0.74 | 111 | 82.14 | 12 | 7.4 | 18.9071 | YES | 896
8 / 8:00 | 0.78 | 111 | 86.58 | 12.1 | 7.39 | 18.8035 | YES | 864
9 / 8:00 | 0.79 | 111 | 87.69 | 12.1 | 7.38 | 18.7595 | YES | 834
10 / 12:00 | 0.75 | 111 | 83.25 | 12 | 7.49 | 19.527 | YES | 821
11 / 8:00 | 0.7 | 111 | 77.7 | 12 | 7.57 | 19.9653 | YES | 844
12 / 12:00 | 0.71 | 111 | 78.81 | 12 | 7.59 | 20.1272 | YES | 857
13 / 8:00 | 0.7 | 111 | 77.7 | 11.9 | 7.47 | 19.4102 | YES | 821
14 / 8:00 | 0.73 | 111 | 81.03 | 11.9 | 7.45 | 19.3407 | YES | 865
15 / 8:00 | 0.75 | 111 | 83.25 | 11.7 | 7.46 | 19.706 | YES | 862
16 / 8:00 | 0.75 | 111 | 83.25 | 11.8 | 7.32 | 18.6527 | YES | 894
17 / 8:00 | 0.74 | 111 | 82.14 | 11.6 | 7.31 | 18.8098 | YES | 885
18 / 8:00 | 0.75 | 111 | 83.25 | 11.6 | 7.42 | 19.5613 | YES | 840
19 / 8:00 | 0.76 | 111 | 84.36 | 10.2 | 7.5 | 22.0738 | YES | 857
20 / 8:00 | 0.76 | 111 | 84.36 | 11 | 7.5 | 20.9418 | YES | 843
21 / 8:00 | 0.73 | 111 | 81.03 | 11 | 7.48 | 20.726 | YES | 834
22 / 8:00 | 0.74 | 111 | 82.14 | 10.8 | 7.5 | 21.1709 | YES | 828
23 / 8:00 | 0.73 | 111 | 81.03 | 10.7 | 7.47 | 21.0642 | YES | 825
24/8:00 | 0.75 | 111 | 83.25 | 10.4 | 7.47 | 21.5321 | YES | 874
25/12:00 | 0.71 | 111 | 78.81 | 10.1 | 7.46 | 21.7863 | YES | 901
26/12:00 | 0.69 | 111 | 76.59 | 9.8 | 7.47 | 22.2498 | YES | 863
27 / 8:00 | 0.69 | 111 | 76.59 | 9.6 | 7.39 | 21.9199 | YES | 864
28 / 8:00 | 0.77 | 111 | 85.47 | 9.2 | 7.4 | 22.7918 | YES | 866
29 / 8:00 | 0.8 | 111 | 88.8 | 8.9 | 7.42 | 23.4946 | YES | 837
30 / 12:00 | 0.79 | 111 | 87.69 | 8.5 | 7.51 | 24.8836 | YES | 869
31 |  | 111 |  |  |  |  | NO
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Nov | 999.99 | 999.99 | 999.99 | 0.13073 | 0.099418 | 999.99 | 12 | 0 | 0.13081 | 999.99 | 999.99 | 999.99 | 0.78684 | 0.81858 | 999.99 | 12 | 0.78684 | 0.79
2 | Nov | 999.99 | 999.99 | 999.99 | 0.12886 | 0.15882 | 999.99 | 16 | 0 | 0.16015 | 999.99 | 999.99 | 999.99 | 0.81364 | 0.82801 | 999.99 | 12 | 0.81364 | 0.81
3 | Nov | 999.99 | 999.99 | 0.14561 | 0.092332 | 0.090036 | 999.99 | 8 | 0 | 0.14586 | 999.99 | 999.99 | 0.79532 | 0.79108 | 0.7978 | 999.99 | 12 | 0.79108 | 0.79
4 | Nov | 999.99 | 999.99 | 999.99 | 0.10694 | 999.99 | 999.99 | 12 | 0 | 0.10694 | 999.99 | 999.99 | 999.99 | 0.73173 | 999.99 | 999.99 | 12 | 0.73173 | 0.73
5 | Nov | 999.99 | 999.99 | 999.99 | 0.1366 | 0.11406 | 999.99 | 0 | 0 | 0 | 999.99 | 999.99 | 999.99 | 0.6464 | 0.69056 | 999.99 | 12 | 0.65 | 0.65
6 | Nov | 999.99 | 999.99 | 0.19348 | 0.12407 | 0.1236 | 999.99 | 0 | 0 | 0 | 999.99 | 999.99 | 0.63421 | 0.6958 | 0.75875 | 999.99 | 8 | 0.64 | 0.64
7 | Nov | 999.99 | 999.99 | 999.99 | 0.03953 | 0.030579 | 999.99 | 0 | 0 | 0 | 999.99 | 999.99 | 999.99 | 0.78255 | 0.84514 | 999.99 | 8 | 0.74 | 0.74
8 | Nov | 999.99 | 999.99 | 999.99 | 0.042317 | 0.058982 | 999.99 | 0 | 0 | 0 | 999.99 | 999.99 | 999.99 | 0.81994 | 0.84561 | 999.99 | 8 | 0.78 | 0.78
9 | Nov | 999.99 | 999.99 | 999.99 | 0.037174 | 0.028145 | 999.99 | 0 | 0 | 0 | 999.99 | 999.99 | 999.99 | 0.80251 | 0.80056 | 999.99 | 8 | 999.99 | 999.99
10 | Nov | 999.99 | 999.99 | 999.99 | 0.03052 | 999.99 | 999.99 | 12 | 0 | 0.031953 | 999.99 | 999.99 | 999.99 | 0.74957 | 999.99 | 999.99 | 12 | 0.74957 | 0.75
11 | Nov | 999.99 | 999.99 | 0.080692 | 0.030697 | 999.99 | 999.99 | 8 | 0 | 0.080692 | 999.99 | 999.99 | 0.71064 | 0.72807 | 999.99 | 999.99 | 8 | 0.71064 | 0.71
12 | Nov | 999.99 | 999.99 | 999.99 | 0.031423 | 0.02628 | 999.99 | 12 | 0 | 0.031443 | 999.99 | 999.99 | 999.99 | 0.70899 | 0.74356 | 999.99 | 12 | 0.70899 | 0.71
13 | Nov | 999.99 | 999.99 | 0.08819 | 0.029401 | 999.99 | 999.99 | 8 | 0 | 0.088289 | 999.99 | 999.99 | 0.70422 | 0.74545 | 999.99 | 999.99 | 8 | 0.70422 | 0.7
14 | Nov | 999.99 | 999.99 | 0.06385 | 0.035035 | 0.032503 | 999.99 | 8 | 0 | 0.067776 | 999.99 | 999.99 | 0.73061 | 0.7667 | 0.77589 | 999.99 | 8 | 0.73061 | 0.73
15 | Nov | 999.99 | 999.99 | 0.052858 | 999.99 | 0.032758 | 999.99 | 8 | 0 | 0.055155 | 999.99 | 999.99 | 0.74839 | 999.99 | 0.75552 | 999.99 | 8 | 0.74839 | 0.75
16 | Nov | 999.99 | 999.99 | 0.033091 | 0.02944 | 0.032424 | 999.99 | 16 | 0 | 0.037135 | 999.99 | 999.99 | 0.75192 | 0.76405 | 0.76847 | 999.99 | 8 | 0.75192 | 0.75
17 | Nov | 999.99 | 999.99 | 0.060239 | 0.044241 | 0.02681 | 999.99 | 8 | 0 | 0.063242 | 999.99 | 999.99 | 0.74038 | 0.75175 | 0.77772 | 999.99 | 8 | 0.74038 | 0.74
18 | Nov | 999.99 | 999.99 | 0.091351 | 0.026045 | 999.99 | 999.99 | 8 | 0 | 0.094805 | 999.99 | 999.99 | 0.74639 | 0.78166 | 999.99 | 999.99 | 8 | 0.74639 | 0.75
19 | Nov | 999.99 | 999.99 | 0.050699 | 0.028695 | 0.030834 | 999.99 | 8 | 0 | 0.053761 | 999.99 | 999.99 | 0.765 | 0.78531 | 0.78272 | 999.99 | 8 | 0.765 | 0.76
20 | Nov | 999.99 | 999.99 | 0.091449 | 0.03264 | 0.03105 | 999.99 | 8 | 0 | 0.097868 | 999.99 | 999.99 | 0.74662 | 0.76682 | 0.77518 | 999.99 | 8 | 0.74662 | 0.75
21 | Nov | 999.99 | 999.99 | 0.061711 | 0.033739 | 999.99 | 999.99 | 8 | 0 | 0.065538 | 999.99 | 999.99 | 0.74321 | 0.76046 | 999.99 | 999.99 | 8 | 0.74321 | 0.74
22 | Nov | 999.99 | 999.99 | 0.037704 | 0.02997 | 999.99 | 999.99 | 8 | 0 | 0.041591 | 999.99 | 999.99 | 0.7435 | 0.76871 | 999.99 | 999.99 | 8 | 0.7435 | 0.74
23 | Nov | 999.99 | 999.99 | 0.061573 | 0.028793 | 0.039549 | 999.99 | 8 | 0 | 0.061946 | 999.99 | 999.99 | 0.72837 | 0.77601 | 0.79338 | 999.99 | 8 | 0.72837 | 0.73
24 | Nov | 999.99 | 999.99 | 0.10484 | 0.030775 | 0.030736 | 999.99 | 8 | 0 | 0.1055 | 999.99 | 999.99 | 0.74974 | 0.77595 | 0.76606 | 999.99 | 8 | 0.74974 | 0.75
25 | Nov | 999.99 | 999.99 | 999.99 | 0.03741 | 0.036389 | 999.99 | 12 | 0 | 0.037528 | 999.99 | 999.99 | 999.99 | 0.71789 | 0.71053 | 999.99 | 16 | 0.71053 | 0.71
26 | Nov | 999.99 | 999.99 | 999.99 | 0.034956 | 0.045419 | 999.99 | 16 | 0 | 0.04797 | 999.99 | 999.99 | 999.99 | 0.6888 | 0.718 | 999.99 | 12 | 0.6888 | 0.69
27 | Nov | 999.99 | 999.99 | 0.098869 | 0.038352 | 999.99 | 999.99 | 8 | 0 | 0.098869 | 999.99 | 999.99 | 0.68803 | 0.75027 | 999.99 | 999.99 | 8 | 0.68803 | 0.69
28 | Nov | 999.99 | 999.99 | 0.062476 | 0.036703 | 999.99 | 999.99 | 8 | 0 | 0.064714 | 999.99 | 999.99 | 0.76729 | 0.81882 | 999.99 | 999.99 | 8 | 0.76729 | 0.77
29 | Nov | 999.99 | 999.99 | 0.066383 | 0.040786 | 0.037371 | 999.99 | 8 | 0 | 0.073331 | 999.99 | 999.99 | 0.7995 | 0.82129 | 0.83454 | 999.99 | 8 | 0.7995 | 0.8
30 | Nov | 999.99 | 999.99 | 0.069523 | 0.046047 | 0.06389 | 999.99 | 8 | 0 | 0.07284 | 999.99 | 999.99 | 0.79603 | 0.80339 | 0.79609 | 999.99 | 8 | 0.79603 | 0.8