## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Jan_24
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | 0.01 | 0.01 | 0.01 | OFF | 0.01
2 | OFF | OFF | 0.01 | 0.01 | OFF | OFF | 0.01
3 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02 | 0.02
4 | OFF | OFF | 0.02 | 0.023375 | 0.02 | OFF | 0.02
5 | OFF | OFF | 0.02 | 0.02 | 0.023434 | 0.02 | 0.02
6 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
7 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
8 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
9 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
10 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
11 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
12 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
13 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
14 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
15 | OFF | OFF | OFF | 0.01 | OFF | OFF | 0.01
16 | 0.01 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02
17 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
18 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
19 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
20 | OFF | OFF | 0.02 | 0.01 | 0.01 | OFF | 0.02
21 | OFF | OFF | 0.01 | 0.01 | 0.01 | OFF | 0.01
22 | OFF | OFF | 0.01 | 0.01 | OFF | OFF | 0.01
23 | OFF | 0.01 | 0.01 | 0.01 | OFF | OFF | 0.01
24 | OFF | 0.02 | OFF | 0.02 | OFF | OFF | 0.02
25 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
26 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
27 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
28 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
29 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
30 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
31 | OFF | OFF | 0.01 | 0.02 | 0.02 | OFF | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME:
[5 empty] | SIGNATURE: |  |  | DATE:
[5 empty] | PHONE #: ( ) |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Jan_24 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 8:00 | 0.75 | 111 | 83.25 | 9.9 | 7.56 | 22.9712 | YES | 854
2 / 8:00 | 0.75 | 111 | 83.25 | 9.9 | 7.51 | 22.5695 | YES | 840
3 / 4:00 | 0.78 | 111 | 86.58 | 9.7 | 7.47 | 22.6267 | YES | 825
4 / 8:00 | 0.76 | 111 | 84.36 | 9.7 | 7.44 | 22.3381 | YES | 807
5 / 20:00 | 0.63 | 111 | 69.93 | 9.8 | 7.35 | 21.1881 | YES | 815
6 / 12:00 | 0.62 | 111 | 68.82 | 9.6 | 7.28 | 20.9252 | YES | 817
7 / 8:00 | 0.68 | 111 | 75.48 | 9.6 | 7.23 | 20.7018 | YES | 821
8 / 4:00 | 0.77 | 111 | 85.47 | 9.2 | 7.18 | 21.0962 | YES | 858
9 / 8:00 | 0.77 | 111 | 85.47 | 9.3 | 7.17 | 20.885 | YES | 830
10 / 12:00 | 0.77 | 111 | 85.47 | 9.1 | 7.21 | 21.4596 | YES | 830
11 / 12:00 | 0.75 | 111 | 83.25 | 9.1 | 7.14 | 20.8931 | YES | 777
12 / 8:00 | 0.74 | 111 | 82.14 | 9.1 | 7.05 | 20.2246 | YES | 832
13 / 16:00 | 0.9 | 111 | 99.9 | 8.9 | 7.22 | 22.1433 | YES | 781
14 / 12:00 | 0.82 | 111 | 91.02 | 8.6 | 7.28 | 22.8616 | YES | 890
15 / 12:00 | 0.88 | 111 | 97.68 | 8.5 | 7.35 | 23.752 | YES | 868
16 / 12:00 | 0.92 | 111 | 102.12 | 8.4 | 7.41 | 24.5369 | YES | 910
17 / 12:00 | 0.88 | 111 | 97.68 | 8.3 | 7.62 | 26.5011 | YES | 812
18 / 8:00 | 0.89 | 111 | 98.79 | 8.3 | 7.55 | 25.8758 | YES | 859
19 / 8:00 | 0.89 | 111 | 98.79 | 8.4 | 7.63 | 26.4485 | YES | 877
20 / 8:00 | 0.89 | 111 | 98.79 | 8.5 | 7.75 | 27.4257 | YES | 874
21 / 8:00 | 0.9 | 111 | 99.9 | 8.7 | 7.66 | 26.231 | YES | 869
22 / 8:00 | 0.91 | 111 | 101.01 | 9.1 | 7.73 | 26.2136 | YES | 880
23 / 4:00 | 0.91 | 111 | 101.01 | 9.2 | 7.65 | 25.3055 | YES | 830
24 / 12:00 | 0.88 | 111 | 97.68 | 9.4 | 7.54 | 23.9303 | YES | 862
25 / 4:00 | 0.85 | 111 | 94.35 | 9.6 | 7.63 | 24.2967 | YES | 835
26 / 8:00 | 0.84 | 111 | 93.24 | 9.6 | 7.66 | 24.529 | YES | 860
27 / 12:00 | 0.85 | 111 | 94.35 | 9.9 | 7.67 | 24.1566 | YES | 855
28 / 8:00 | 0.85 | 111 | 94.35 | 10 | 7.7 | 24.2531 | YES | 869
29 / 16:00 | 0.87 | 111 | 96.57 | 10.1 | 7.67 | 23.8915 | YES | 909
30 / 12:00 | 0.88 | 111 | 97.68 | 10.4 | 7.67 | 23.4465 | YES | 895
31 / 8:00 | 0.86 | 111 | 95.46 | 10.7 | 7.52 | 21.7527 | YES | 883
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Jan | 999.99 | 999.99 | 0.11065 | 0.087484 | 0.090683 | 999.99 | 8 | 0 | 0.11065 | 999.99 | 999.99 | 0.75181 | 0.769 | 0.76588 | 999.99 | 8 | 0.75181 | 0.75
2 | Jan | 999.99 | 999.99 | 0.11991 | 0.097593 | 999.99 | 999.99 | 8 | 0 | 0.12056 | 999.99 | 999.99 | 0.75186 | 0.78455 | 999.99 | 999.99 | 8 | 0.75186 | 0.75
3 | Jan | 999.99 | 0.036213 | 0.021648 | 999.99 | 999.99 | 0.028616 | 4 | 0 | 0.036213 | 999.99 | 0.77418 | 0.79385 | 999.99 | 999.99 | 0.78484 | 4 | 0.77418 | 0.77
4 | Jan | 999.99 | 999.99 | 0.048893 | 0.023375 | 0.027752 | 999.99 | 8 | 0 | 0.048893 | 999.99 | 999.99 | 0.76217 | 0.79409 | 0.77707 | 999.99 | 8 | 0.76217 | 0.76
5 | Jan | 999.99 | 999.99 | 0.040276 | 0.026535 | 0.023434 | 0.036232 | 8 | 0 | 0.041336 | 999.99 | 999.99 | 0.67979 | 0.64816 | 0.64216 | 0.63409 | 20 | 0.63409 | 0.63
6 | Jan | 999.99 | 999.99 | 999.99 | 0.029696 | 0.055626 | 999.99 | 16 | 0 | 0.055626 | 999.99 | 999.99 | 999.99 | 0.62602 | 0.65959 | 999.99 | 12 | 0.62602 | 0.63
7 | Jan | 999.99 | 999.99 | 0.04852 | 0.03103 | 0.032719 | 999.99 | 8 | 0 | 0.074038 | 999.99 | 999.99 | 0.68656 | 0.74403 | 0.76193 | 999.99 | 8 | 0.68656 | 0.69
8 | Jan | 999.99 | 0.03898 | 0.03739 | 0.039628 | 0.039844 | 999.99 | 16 | 0 | 0.041061 | 999.99 | 0.76729 | 0.77901 | 0.79538 | 0.79061 | 999.99 | 4 | 0.76729 | 0.77
9 | Jan | 999.99 | 999.99 | 0.054939 | 0.035722 | 0.038058 | 999.99 | 8 | 0 | 0.057216 | 999.99 | 999.99 | 0.7627 | 0.76847 | 0.80639 | 999.99 | 8 | 0.7627 | 0.76
10 | Jan | 999.99 | 999.99 | 0.051818 | 0.039432 | 999.99 | 0.040433 | 8 | 0 | 0.055469 | 999.99 | 999.99 | 0.77277 | 0.77677 | 999.99 | 0.79456 | 12 | 0.77277 | 0.77
11 | Jan | 999.99 | 999.99 | 999.99 | 0.045752 | 0.042317 | 999.99 | 12 | 0 | 0.045752 | 999.99 | 999.99 | 999.99 | 0.7561 | 0.76011 | 999.99 | 12 | 0.7561 | 0.76
12 | Jan | 999.99 | 999.99 | 0.0623 | 0.042749 | 0.039707 | 0.041296 | 8 | 0 | 0.062555 | 999.99 | 999.99 | 0.73944 | 0.77418 | 0.86069 | 0.94666 | 8 | 0.73944 | 0.74
13 | Jan | 999.99 | 999.99 | 999.99 | 0.050463 | 0.044732 | 999.99 | 12 | 0 | 0.050797 | 999.99 | 999.99 | 999.99 | 0.92117 | 0.89897 | 999.99 | 16 | 0.89897 | 0.9
14 | Jan | 999.99 | 999.99 | 999.99 | 0.055351 | 999.99 | 999.99 | 12 | 0 | 0.055724 | 999.99 | 999.99 | 999.99 | 0.82259 | 999.99 | 999.99 | 12 | 0.82259 | 0.82
15 | Jan | 999.99 | 999.99 | 999.99 | 0.045006 | 999.99 | 999.99 | 12 | 0 | 0.04905 | 999.99 | 999.99 | 999.99 | 0.87347 | 999.99 | 999.99 | 12 | 0.87347 | 0.87
16 | Jan | 0.04638 | 999.99 | 999.99 | 0.048422 | 0.041866 | 0.036546 | 0 | 0 | 0.049286 | 0.9065 | 999.99 | 999.99 | 0.92228 | 0.92741 | 0.9323 | 12 | 0.92228 | 0.92
17 | Jan | 999.99 | 0.045556 | 0.040609 | 0.039785 | 0.038038 | 0.045046 | 4 | 0 | 0.045909 | 999.99 | 0.9068 | 0.89543 | 0.88083 | 0.88589 | 0.88324 | 12 | 0.88083 | 0.88
18 | Jan | 999.99 | 999.99 | 0.046518 | 0.044614 | 0.043043 | 999.99 | 8 | 0 | 0.04691 | 999.99 | 999.99 | 0.89261 | 0.91045 | 0.90362 | 999.99 | 8 | 0.89261 | 0.89
19 | Jan | 999.99 | 999.99 | 0.074607 | 0.050483 | 0.047519 | 0.049776 | 8 | 0 | 0.074745 | 999.99 | 999.99 | 0.87906 | 0.90126 | 0.89732 | 0.89496 | 8 | 0.87906 | 0.88
20 | Jan | 999.99 | 999.99 | 0.062535 | 0.062025 | 0.060121 | 999.99 | 12 | 0 | 0.063124 | 999.99 | 999.99 | 0.89078 | 0.90167 | 0.9244 | 999.99 | 8 | 0.89078 | 0.89
21 | Jan | 999.99 | 999.99 | 0.1026 | 0.070838 | 0.076295 | 999.99 | 8 | 0 | 0.10348 | 999.99 | 999.99 | 0.89066 | 0.90238 | 0.92446 | 999.99 | 8 | 0.89066 | 0.89
22 | Jan | 999.99 | 999.99 | 0.11496 | 0.07869 | 999.99 | 999.99 | 8 | 0 | 0.11606 | 999.99 | 999.99 | 0.90232 | 0.92488 | 999.99 | 999.99 | 8 | 0.90232 | 0.9
23 | Jan | 999.99 | 0.15199 | 0.093844 | 0.087248 | 999.99 | 999.99 | 4 | 0 | 0.16045 | 999.99 | 0.90986 | 0.92605 | 0.93312 | 999.99 | 999.99 | 4 | 0.90986 | 0.91
24 | Jan | 999.99 | 0.099438 | 999.99 | 0.096572 | 999.99 | 999.99 | 4 | 0 | 0.10069 | 999.99 | 0.89414 | 999.99 | 0.88124 | 999.99 | 999.99 | 12 | 0.88124 | 0.88
25 | Jan | 999.99 | 0.16441 | 0.11451 | 0.10872 | 999.99 | 999.99 | 4 | 0 | 0.16498 | 999.99 | 0.85009 | 0.85686 | 0.86581 | 999.99 | 999.99 | 4 | 0.85009 | 0.85
26 | Jan | 999.99 | 999.99 | 0.17619 | 0.12258 | 0.11846 | 999.99 | 8 | 0 | 0.17619 | 999.99 | 999.99 | 0.8389 | 0.86428 | 0.87335 | 999.99 | 8 | 0.8389 | 0.84
27 | Jan | 999.99 | 999.99 | 999.99 | 0.14484 | 0.13612 | 999.99 | 12 | 0 | 0.14686 | 999.99 | 999.99 | 999.99 | 0.86375 | 0.87447 | 999.99 | 12 | 0.86375 | 0.86
28 | Jan | 999.99 | 999.99 | 0.19399 | 0.14861 | 0.14604 | 999.99 | 8 | 0 | 0.19539 | 999.99 | 999.99 | 0.84897 | 0.86852 | 0.87435 | 999.99 | 8 | 0.84897 | 0.85
29 | Jan | 999.99 | 999.99 | 999.99 | 0.1626 | 0.16649 | 999.99 | 16 | 0 | 0.1672 | 999.99 | 999.99 | 999.99 | 0.87241 | 0.86157 | 999.99 | 16 | 0.86157 | 0.86
30 | Jan | 999.99 | 999.99 | 999.99 | 0.17354 | 0.16967 | 999.99 | 12 | 0 | 0.17727 | 999.99 | 999.99 | 999.99 | 0.874 | 0.88283 | 999.99 | 12 | 0.874 | 0.87
31 | Jan | 999.99 | 999.99 | 0.23896 | 0.17905 | 0.17807 | 999.99 | 8 | 0 | 0.24189 | 999.99 | 999.99 | 0.86846 | 0.87618 | 0.88542 | 999.99 | 8 | 0.86846 | 0.87