## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Feb_24
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
2 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
3 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
4 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
5 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
6 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
7 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
8 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
9 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
10 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
11 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
12 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
13 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
14 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
15 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
16 | OFF | 0.02 | 0.02 | OFF | 0.02 | OFF | 0.02
17 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
18 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
19 | OFF | OFF | 0.02 | 0.03 | 0.02 | OFF | 0.03
20 | OFF | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02
21 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
22 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
23 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
24 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
25 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
26 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
27 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
28 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
29 | OFF | OFF | OFF | 0.02 | 0.03 | 0.029931 | 0.03
30
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:03/01/2024
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Feb_24 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 8:00 | 0.86 | 111 | 95.46 | 10.8 | 7.95 | 25.1587 | YES | 885
2 / 8:00 | 0.87 | 111 | 96.57 | 10.5 | 7.72 | 23.6803 | YES | 854
3 / 20:00 | 0.85 | 111 | 94.35 | 10.7 | 7.64 | 22.6653 | YES | 814
4 / 12:00 | 0.75 | 111 | 83.25 | 10.5 | 7.59 | 22.3118 | YES | 851
5 / 8:00 | 0.7 | 111 | 77.7 | 10.3 | 7.46 | 21.4771 | YES | 894
6 / 8:00 | 0.73 | 111 | 81.03 | 10.8 | 7.5 | 21.1471 | YES | 885
7 / 8:00 | 0.74 | 111 | 82.14 | 9.9 | 7.51 | 22.544 | YES | 853
8 / 8:00 | 0.75 | 111 | 83.25 | 9.8 | 7.53 | 22.8803 | YES | 901
9 / 8:00 | 0.76 | 111 | 84.36 | 9.8 | 7.56 | 23.1502 | YES | 838
10 / 8:00 | 0.75 | 111 | 83.25 | 9.8 | 7.44 | 22.166 | YES | 833
11 / 8:00 | 0.75 | 111 | 83.25 | 9.7 | 7.5 | 22.7897 | YES | 873
12 / 8:00 | 0.76 | 111 | 84.36 | 9.5 | 7.4 | 22.3187 | YES | 825
13 / 16:00 | 0.76 | 111 | 84.36 | 9.5 | 7.52 | 23.284 | YES | 826
14 / 8:00 | 0.75 | 111 | 83.25 | 9.5 | 7.48 | 22.9312 | YES | 881
15 / 12:00 | 0.77 | 111 | 85.47 | 9.5 | 7.51 | 23.2282 | YES | 874
16 / 4:00 | 0.76 | 111 | 84.36 | 9.3 | 7.45 | 23.0184 | YES | 863
17 / 12:00 | 0.79 | 111 | 87.69 | 9.4 | 7.49 | 23.2709 | YES | 879
18 / 12:00 | 0.79 | 111 | 87.69 | 9.2 | 7.47 | 23.4156 | YES | 880
19 / 16:00 | 0.79 | 111 | 87.69 | 9.4 | 7.46 | 23.0255 | YES | 815
20 / 8:00 | 0.77 | 111 | 85.47 | 9.6 | 7.39 | 22.1189 | YES | 840
21 / 8:00 | 0.81 | 111 | 89.91 | 9.7 | 7.48 | 22.7839 | YES | 869
22 / 20:00 | 0.82 | 111 | 91.02 | 9.9 | 7.48 | 22.5099 | YES | 830
23 / 8:00 | 0.8 | 111 | 88.8 | 10 | 7.5 | 22.4687 | YES | 823
24 / 8:00 | 0.79 | 111 | 87.69 | 10 | 7.45 | 22.0518 | YES | 848
25 / 8:00 | 0.8 | 111 | 88.8 | 10 | 7.44 | 21.9993 | YES | 858
26 / 8:00 | 0.8 | 111 | 88.8 | 9.9 | 7.36 | 21.5313 | YES | 895
27 / 8:00 | 0.81 | 111 | 89.91 | 9.5 | 7.5 | 23.2516 | YES | 877
28 / 8:00 | 0.81 | 111 | 89.91 | 9.5 | 7.51 | 23.334 | YES | 903
29 / 20:00 | 0.75 | 111 | 83.25 | 9.3 | 7.52 | 23.5684 | YES | 791
30 |  | 111 |  |  |  |  | NO
31 |  | 111 |  |  |  |  | NO
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Feb | 999.99 | 999.99 | 0.2223 | 0.18997 | 0.18638 | 999.99 | 8 | 0 | 0.22351 | 999.99 | 999.99 | 0.86764 | 0.88407 | 0.88901 | 999.99 | 8 | 0.86764 | 0.87
2 | Feb | 999.99 | 999.99 | 0.22718 | 0.20037 | 0.050954 | 999.99 | 8 | 0 | 0.22983 | 999.99 | 999.99 | 0.87164 | 0.87382 | 0.87753 | 999.99 | 8 | 0.87164 | 0.87
3 | Feb | 999.99 | 999.99 | 999.99 | 0.053702 | 0.046302 | 999.99 | 12 | 0 | 0.053741 | 999.99 | 999.99 | 999.99 | 0.84226 | 0.80062 | 999.99 | 20 | 0.80062 | 0.8
4 | Feb | 999.99 | 999.99 | 0.09141 | 0.045909 | 999.99 | 999.99 | 8 | 0 | 0.091606 | 999.99 | 999.99 | 0.75493 | 0.74615 | 999.99 | 999.99 | 12 | 0.74615 | 0.75
5 | Feb | 999.99 | 999.99 | 0.082969 | 0.045949 | 0.042945 | 999.99 | 8 | 0 | 0.083794 | 999.99 | 999.99 | 0.69598 | 0.71011 | 0.73449 | 999.99 | 8 | 0.69598 | 0.7
6 | Feb | 999.99 | 999.99 | 0.071309 | 0.046302 | 0.04269 | 999.99 | 8 | 0 | 0.07337 | 999.99 | 999.99 | 0.73214 | 0.74815 | 0.75045 | 999.99 | 8 | 0.73214 | 0.73
7 | Feb | 999.99 | 999.99 | 0.083774 | 0.045144 | 0.047323 | 999.99 | 8 | 0 | 0.086149 | 999.99 | 999.99 | 0.73661 | 0.75805 | 0.76241 | 999.99 | 8 | 0.73661 | 0.74
8 | Feb | 999.99 | 999.99 | 0.089054 | 0.050306 | 999.99 | 999.99 | 8 | 0 | 0.093078 | 999.99 | 999.99 | 0.7521 | 0.76276 | 999.99 | 999.99 | 8 | 0.7521 | 0.75
9 | Feb | 999.99 | 999.99 | 0.083126 | 0.04479 | 999.99 | 999.99 | 8 | 0 | 0.087072 | 999.99 | 999.99 | 0.75528 | 0.76912 | 999.99 | 999.99 | 8 | 0.75528 | 0.76
10 | Feb | 999.99 | 999.99 | 0.073469 | 0.050306 | 0.051425 | 999.99 | 8 | 0 | 0.073469 | 999.99 | 999.99 | 0.75016 | 0.76741 | 0.77666 | 999.99 | 8 | 0.75016 | 0.75
11 | Feb | 999.99 | 999.99 | 0.10064 | 0.05168 | 0.049521 | 999.99 | 8 | 0 | 0.1038 | 999.99 | 999.99 | 0.75681 | 0.76641 | 0.7637 | 999.99 | 8 | 0.75681 | 0.76
12 | Feb | 999.99 | 999.99 | 0.093628 | 0.054919 | 999.99 | 0.068758 | 8 | 0 | 0.098574 | 999.99 | 999.99 | 0.74515 | 0.76323 | 999.99 | 0.76382 | 8 | 0.74515 | 0.75
13 | Feb | 999.99 | 999.99 | 0.052426 | 999.99 | 0.097612 | 999.99 | 16 | 0 | 0.097907 | 999.99 | 999.99 | 0.76347 | 999.99 | 0.7541 | 999.99 | 16 | 0.7541 | 0.75
14 | Feb | 999.99 | 999.99 | 0.090507 | 0.052544 | 0.050208 | 999.99 | 8 | 0 | 0.098103 | 999.99 | 999.99 | 0.75234 | 0.7627 | 0.77442 | 999.99 | 8 | 0.75 | 0.75
15 | Feb | 999.99 | 999.99 | 999.99 | 0.065087 | 999.99 | 999.99 | 12 | 0 | 0.065853 | 999.99 | 999.99 | 999.99 | 0.76635 | 999.99 | 999.99 | 12 | 0.76635 | 0.77
16 | Feb | 999.99 | 0.085187 | 0.053957 | 999.99 | 0.050522 | 999.99 | 4 | 0 | 0.096101 | 999.99 | 0.76199 | 0.78655 | 999.99 | 0.81046 | 999.99 | 4 | 0.76199 | 0.76
17 | Feb | 999.99 | 999.99 | 999.99 | 0.057118 | 0.053447 | 999.99 | 12 | 0 | 0.057275 | 999.99 | 999.99 | 999.99 | 0.7968 | 0.81399 | 999.99 | 12 | 0.7968 | 0.8
18 | Feb | 999.99 | 999.99 | 999.99 | 0.069209 | 0.05435 | 999.99 | 8 | 0 | 0.092686 | 999.99 | 999.99 | 999.99 | 0.79185 | 0.81888 | 999.99 | 12 | 0.79185 | 0.79
19 | Feb | 999.99 | 999.99 | 0.10005 | 0.059571 | 0.056961 | 999.99 | 8 | 0 | 0.10038 | 999.99 | 999.99 | 0.79562 | 0.80592 | 0.79291 | 999.99 | 16 | 0.79291 | 0.79
20 | Feb | 999.99 | 999.99 | 0.070544 | 999.99 | 0.2933 | 0.13609 | 16 | 0 | 0.2971 | 999.99 | 999.99 | 0.76853 | 999.99 | 0.79415 | 0.8091 | 8 | 0.76853 | 0.77
21 | Feb | 999.99 | 999.99 | 0.12127 | 999.99 | 0.43302 | 999.99 | 16 | 0 | 0.43437 | 999.99 | 999.99 | 0.79562 | 999.99 | 0.84367 | 999.99 | 8 | 0.79562 | 0.8
22 | Feb | 999.99 | 999.99 | 0.19474 | 0.14761 | 0.13614 | 0.1037 | 8 | 0 | 0.19474 | 999.99 | 999.99 | 0.83054 | 0.83413 | 0.83048 | 0.82983 | 20 | 0.82983 | 0.83
23 | Feb | 999.99 | 999.99 | 0.13163 | 999.99 | 0.24238 | 999.99 | 16 | 0 | 0.24238 | 999.99 | 999.99 | 0.80174 | 999.99 | 0.81217 | 999.99 | 8 | 0.80174 | 0.8
24 | Feb | 999.99 | 999.99 | 0.10725 | 0.073233 | 0.057667 | 999.99 | 8 | 0 | 0.11051 | 999.99 | 999.99 | 0.78967 | 0.79644 | 0.81175 | 999.99 | 8 | 0.78967 | 0.79
25 | Feb | 999.99 | 999.99 | 0.079632 | 0.039 | 0.049344 | 999.99 | 8 | 0 | 0.084638 | 999.99 | 999.99 | 0.80174 | 0.8147 | 0.80899 | 999.99 | 8 | 0.80174 | 0.8
26 | Feb | 999.99 | 999.99 | 0.069994 | 0.035859 | 0.032208 | 999.99 | 8 | 0 | 0.10497 | 999.99 | 999.99 | 0.7889 | 0.81458 | 0.82377 | 999.99 | 8 | 0.7889 | 0.79
27 | Feb | 999.99 | 999.99 | 0.066579 | 0.030324 | 0.031168 | 999.99 | 8 | 0 | 0.066598 | 999.99 | 999.99 | 0.80639 | 0.82754 | 0.83254 | 999.99 | 8 | 0.80639 | 0.81
28 | Feb | 999.99 | 999.99 | 0.049658 | 0.043161 | 999.99 | 0.044594 | 8 | 0 | 0.049658 | 999.99 | 999.99 | 0.81487 | 0.82224 | 999.99 | 0.81641 | 8 | 0.81487 | 0.81
29 | Feb | 999.99 | 999.99 | 999.99 | 0.044162 | 0.031698 | 0.029931 | 12 | 0 | 0.04589 | 999.99 | 999.99 | 999.99 | 0.81305 | 0.80109 | 0.75304 | 20 | 0.75304 | 0.75