## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Apr_24
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | 0.03 | 0.03474 | 0.03 | OFF | 0.03
2 | OFF | OFF | 0.03 | OFF | 0.03 | OFF | 0.03
3 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
4 | OFF | OFF | 0.03 | 0.034269 | 0.032247 | OFF | 0.03
5 | OFF | OFF | 0.03 | 0.03 | OFF | OFF | 0.03
6 | OFF | OFF | OFF | 0.03 | 0.03 | OFF | 0.03
7 | OFF | OFF | OFF | 0.03 | 0.03 | OFF | 0.03
8 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
9 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
10 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
11 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
12 | OFF | OFF | 0.03 | 0.04 | 0.03 | OFF | 0.04
13 | OFF | OFF | OFF | 0.03 | 0.03 | OFF | 0.03
14 | OFF | OFF | OFF | 0.03 | 0.03 | OFF | 0.03
15 | OFF | OFF | 0.07 | 0.023 | 0.03 | OFF | 0.07
16 | OFF | OFF | OFF | 0.03 | 0.03 | OFF | 0.03
17 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
18 | OFF | OFF | OFF | 0.04 | 0.03 | 0.03 | 0.04
19 | OFF | OFF | OFF | 0.03 | 0.03 | OFF | 0.03
20 | OFF | OFF | OFF | 0.03 | OFF | OFF | 0.03
21 | OFF | OFF | 0.04 | 0.04 | 0.04 | OFF | 0.04
22 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
23 | OFF | OFF | 0.03 | 0.04 | 0.03 | 0.03 | 0.04
24 | OFF | OFF | OFF | 0.03 | 0.03 | OFF | 0.03
25 | OFF | OFF | 0.03 | 0.03 | OFF | OFF | 0.03
26 | OFF | OFF | 0.06 | 0.03 | 0.03 | OFF | 0.06
27 | OFF | OFF | OFF | 0.03 | 0.03 | OFF | 0.03
28 | OFF | OFF | OFF | 0.03 | 0.03 | OFF | 0.03
29 | OFF | OFF | OFF | 0.03 | 0.02 | OFF | 0.03
30 | OFF | OFF | 0.075216 | 0.02 | 0.02 | OFF | 0.02
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:05/01/2024
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Apr_24 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 8:00 | 0.8 | 111 | 88.8 | 10.2 | 7.32 | 20.8176 | YES | 753
2 / 16:00 | 0.8 | 111 | 88.8 | 10.4 | 7.39 | 21.0553 | YES | 800
3 / 8:00 | 0.77 | 111 | 85.47 | 10.3 | 7.44 | 21.4958 | YES | 781
4 / 8:00 | 0.79 | 111 | 87.69 | 10.3 | 7.37 | 21.0225 | YES | 824
5 / 8:00 | 0.79 | 111 | 87.69 | 10.1 | 7.3 | 20.7853 | YES | 830
6 / 12:00 | 0.77 | 111 | 85.47 | 10.1 | 7.4 | 21.4772 | YES | 826
7 / 12:00 | 0.79 | 111 | 87.69 | 10 | 7.41 | 21.7441 | YES | 846
8 / 12:00 | 0.78 | 111 | 86.58 | 10.3 | 7.43 | 21.4448 | YES | 761
9 / 8:00 | 0.77 | 111 | 85.47 | 10.4 | 7.53 | 22.0403 | YES | 779
10 / 8:00 | 0.76 | 111 | 84.36 | 10.4 | 7.5 | 21.7846 | YES | 765
11 / 8:00 | 0.78 | 111 | 86.58 | 10.6 | 7.49 | 21.4726 | YES | 762
12 / 8:00 | 0.76 | 111 | 84.36 | 10.7 | 7.46 | 21.0615 | YES | 823
13 / 12:00 | 0.78 | 111 | 86.58 | 10.8 | 7.5 | 21.2664 | YES | 832
14 / 12:00 | 0.76 | 111 | 84.36 | 10.7 | 7.45 | 20.988 | YES | 801
15 / 8:00 | 0.74 | 111 | 82.14 | 10.7 | 7.5 | 21.3105 | YES | 840
16 / 12:00 | 0.78 | 111 | 86.58 | 10.7 | 7.41 | 20.7431 | YES | 812
17 / 8:00 | 0.79 | 111 | 87.69 | 10.6 | 7.43 | 21.0498 | YES | 787
18 / 12:00 | 0.77 | 111 | 85.47 | 11 | 7.5 | 20.9653 | YES | 786
19 / 12:00 | 0.77 | 111 | 85.47 | 11 | 7.36 | 19.9664 | YES | 774
20 / 12:00 | 0.75 | 111 | 83.25 | 11.3 | 7.41 | 19.8783 | YES | 795
21 / 8:00 | 0.74 | 111 | 82.14 | 11.2 | 7.4 | 19.9167 | YES | 806
22 / 8:00 | 0.77 | 111 | 85.47 | 11.2 | 7.43 | 20.1933 | YES | 838
23 / 8:00 | 0.81 | 111 | 89.91 | 11.2 | 7.41 | 20.1431 | YES | 829
24 / 12:00 | 0.82 | 111 | 91.02 | 11.4 | 7.42 | 19.9734 | YES | 824
25 / 8:00 | 0.8 | 111 | 88.8 | 11.4 | 7.36 | 19.5179 | YES | 815
26 / 8:00 | 0.77 | 111 | 85.47 | 11.2 | 7.33 | 19.5037 | YES | 785
27 / 12:00 | 0.76 | 111 | 84.36 | 11.1 | 7.28 | 19.2723 | YES | 805
28 / 16:00 | 0.72 | 111 | 79.92 | 10.9 | 7.24 | 19.1703 | YES | 767
29 / 12:00 | 0.69 | 111 | 76.59 | 11 | 7.27 | 19.1809 | YES | 785
30 / 12:00 | 0.7 | 111 | 77.7 | 11.1 | 7.37 | 19.7507 | YES | 811
31 |  | 111 |  |  |  |  | NO
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Apr | 999.99 | 999.99 | 0.13399 | 0.03474 | 0.038784 | 999.99 | 8 | 0 | 0.13656 | 999.99 | 999.99 | 0.81217 | 0.85827 | 0.84131 | 999.99 | 8 | 0.81217 | 0.81
2 | Apr | 999.99 | 0.082243 | 0.043809 | 0.060455 | 0.04112 | 999.99 | 4 | 0 | 0.084049 | 999.99 | 0.81116 | 0.80904 | 0.78696 | 0.80398 | 999.99 | 16 | 0.8 | 0.8
3 | Apr | 999.99 | 999.99 | 0.053172 | 0.034976 | 999.99 | 999.99 | 8 | 0 | 0.056725 | 999.99 | 999.99 | 0.77489 | 0.81022 | 999.99 | 999.99 | 8 | 0.77489 | 0.77
4 | Apr | 999.99 | 999.99 | 0.05223 | 0.034269 | 0.032247 | 999.99 | 8 | 0 | 0.05223 | 999.99 | 999.99 | 0.80233 | 0.83437 | 0.83278 | 999.99 | 8 | 0.80233 | 0.8
5 | Apr | 999.99 | 999.99 | 0.060926 | 0.08346 | 999.99 | 999.99 | 12 | 0 | 0.08346 | 999.99 | 999.99 | 0.79026 | 0.76199 | 999.99 | 999.99 | 12 | 0.76199 | 0.76
6 | Apr | 999.99 | 999.99 | 0.095159 | 0.041532 | 0.046891 | 999.99 | 8 | 0 | 0.098928 | 999.99 | 999.99 | 0.75216 | 0.77518 | 0.78926 | 999.99 | 8 | 0.75216 | 0.75
7 | Apr | 999.99 | 999.99 | 0.090487 | 0.046832 | 0.04695 | 999.99 | 8 | 0 | 0.090958 | 999.99 | 999.99 | 0.75952 | 0.7806 | 0.80239 | 999.99 | 8 | 0.75952 | 0.76
8 | Apr | 999.99 | 999.99 | 0.070367 | 0.07021 | 0.04322 | 999.99 | 8 | 0 | 0.073351 | 999.99 | 999.99 | 0.77577 | 0.76871 | 0.79992 | 999.99 | 12 | 0.76871 | 0.77
9 | Apr | 999.99 | 999.99 | 0.057157 | 0.044457 | 0.047048 | 999.99 | 8 | 0 | 0.059198 | 999.99 | 999.99 | 0.77948 | 0.78661 | 0.78708 | 999.99 | 8 | 0.77948 | 0.78
10 | Apr | 999.99 | 999.99 | 0.070838 | 0.050561 | 0.052485 | 999.99 | 8 | 0 | 0.075432 | 999.99 | 999.99 | 0.77607 | 0.79821 | 0.7995 | 999.99 | 8 | 0.77607 | 0.78
11 | Apr | 999.99 | 999.99 | 0.066697 | 0.15544 | 999.99 | 999.99 | 12 | 0 | 0.15544 | 999.99 | 999.99 | 0.77995 | 0.73726 | 999.99 | 999.99 | 8 | 0.78 | 0.78
12 | Apr | 999.99 | 999.99 | 0.21034 | 0.059277 | 0.059139 | 999.99 | 8 | 0 | 0.21036 | 999.99 | 999.99 | 0.76064 | 0.78932 | 0.78779 | 999.99 | 8 | 0.76064 | 0.76
13 | Apr | 999.99 | 999.99 | 0.11546 | 0.069464 | 0.074332 | 999.99 | 8 | 0 | 0.11777 | 999.99 | 999.99 | 0.76217 | 0.77648 | 0.78325 | 999.99 | 8 | 0.76217 | 0.76
14 | Apr | 999.99 | 999.99 | 0.13442 | 0.13251 | 0.083951 | 999.99 | 12 | 0 | 0.13997 | 999.99 | 999.99 | 0.75345 | 0.76782 | 0.78125 | 999.99 | 12 | 0.76 | 0.76
15 | Apr | 999.99 | 999.99 | 0.1309 | 0.087484 | 0.085403 | 999.99 | 8 | 0 | 0.13198 | 999.99 | 999.99 | 0.75699 | 0.78001 | 0.79921 | 999.99 | 8 | 0.75699 | 0.76
16 | Apr | 999.99 | 999.99 | 999.99 | 0.10721 | 0.09722 | 999.99 | 12 | 0 | 0.12242 | 999.99 | 999.99 | 999.99 | 0.78667 | 0.82494 | 999.99 | 12 | 0.78667 | 0.79
17 | Apr | 999.99 | 999.99 | 0.12872 | 0.1799 | 0.035054 | 999.99 | 12 | 0 | 0.1799 | 999.99 | 999.99 | 0.80639 | 0.78814 | 0.81782 | 999.99 | 8 | 0.79 | 0.79
18 | Apr | 999.99 | 999.99 | 999.99 | 0.049286 | 0.041669 | 999.99 | 12 | 0 | 0.049286 | 999.99 | 999.99 | 999.99 | 0.77595 | 0.78284 | 999.99 | 12 | 0.77595 | 0.78
19 | Apr | 999.99 | 999.99 | 999.99 | 0.043416 | 0.044005 | 999.99 | 12 | 0 | 0.04532 | 999.99 | 999.99 | 999.99 | 0.7604 | 0.76741 | 999.99 | 12 | 0.7604 | 0.76
20 | Apr | 999.99 | 999.99 | 0.093019 | 0.073704 | 999.99 | 999.99 | 8 | 0 | 0.097632 | 999.99 | 999.99 | 0.74456 | 0.76588 | 999.99 | 999.99 | 8 | 0.74456 | 0.74
21 | Apr | 999.99 | 999.99 | 0.07076 | 0.045713 | 0.043024 | 999.99 | 8 | 0 | 0.071584 | 999.99 | 999.99 | 0.74957 | 0.77324 | 0.78678 | 999.99 | 8 | 0.74957 | 0.75
22 | Apr | 999.99 | 999.99 | 0.072252 | 0.048147 | 999.99 | 999.99 | 8 | 0 | 0.076236 | 999.99 | 999.99 | 0.77265 | 0.80439 | 999.99 | 999.99 | 8 | 0.77265 | 0.77
23 | Apr | 999.99 | 999.99 | 0.073567 | 0.15668 | 0.046969 | 999.99 | 12 | 0 | 0.1567 | 999.99 | 999.99 | 0.8091 | 0.81911 | 0.85168 | 999.99 | 8 | 0.8091 | 0.81
24 | Apr | 999.99 | 999.99 | 999.99 | 0.066775 | 0.043416 | 999.99 | 12 | 0 | 0.066893 | 999.99 | 999.99 | 999.99 | 0.82065 | 0.83884 | 999.99 | 12 | 0.82065 | 0.82
25 | Apr | 999.99 | 999.99 | 0.087464 | 0.048579 | 999.99 | 999.99 | 8 | 0 | 0.087641 | 999.99 | 999.99 | 0.80268 | 0.80492 | 999.99 | 999.99 | 8 | 0.80268 | 0.8
26 | Apr | 999.99 | 999.99 | 0.086149 | 0.10181 | 0.044496 | 999.99 | 12 | 0 | 0.10181 | 999.99 | 999.99 | 0.76959 | 0.77577 | 0.78667 | 999.99 | 8 | 0.76959 | 0.77
27 | Apr | 999.99 | 999.99 | 999.99 | 0.047637 | 0.048795 | 999.99 | 16 | 0 | 0.048795 | 999.99 | 999.99 | 999.99 | 0.765 | 0.76382 | 999.99 | 16 | 0.76382 | 0.76
28 | Apr | 999.99 | 999.99 | 0.093981 | 0.048913 | 0.047421 | 999.99 | 8 | 0 | 0.093981 | 999.99 | 999.99 | 0.73237 | 0.72219 | 0.72607 | 999.99 | 16 | 0.72 | 0.72
29 | Apr | 999.99 | 999.99 | 999.99 | 0.14033 | 0.052662 | 999.99 | 12 | 0 | 0.14035 | 999.99 | 999.99 | 999.99 | 0.71076 | 0.72607 | 999.99 | 12 | 0.71076 | 0.71
30 | Apr | 999.99 | 999.99 | 0.075216 | 0.051013 | 0.047519 | 999.99 | 8 | 0 | 0.075216 | 999.99 | 999.99 | 0.6961 | 0.73019 | 0.75375 | 999.99 | 12 | 0.6961 | 0.7