## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | May_24
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
2 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
3 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
4 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
5 | OFF | OFF | 0.03 | 0.02 | 0.02 | OFF | 0.03
6 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
7 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
8 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
9 | OFF | 0.02 | 0.02 | 0.03 | 0.02 | OFF | 0.03
10 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
11 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
12 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
13 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
14 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
15 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
16 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
17 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
18 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
19 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
20 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
21 | OFF | OFF | 0.02 | 0.01 | OFF | OFF | 0.02
22 | OFF | OFF | 0.02 | 0.01 | 0.02 | OFF | 0.02
23 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
24 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
25 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
26 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
27 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
28 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
29 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
30 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
31 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:06/03/2024
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | May_24 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 12:00 | 0.73 | 111 | 81.03 | 11.1 | 7.34 | 19.6116 | YES | 826
2 / 12:00 | 0.71 | 111 | 78.81 | 11.2 | 7.15 | 18.2069 | YES | 831
3 / 12:00 | 0.79 | 111 | 87.69 | 11.3 | 7.2 | 18.5673 | YES | 833
4 / 12:00 | 0.83 | 111 | 92.13 | 11.3 | 7.25 | 18.9744 | YES | 820
5 / 8:00 | 0.86 | 111 | 95.46 | 11.1 | 7.33 | 19.8292 | YES | 788
6 / 16:00 | 0.86 | 111 | 95.46 | 11 | 7.36 | 20.1683 | YES | 745
7 / 12:00 | 0.81 | 111 | 89.91 | 11 | 7.38 | 20.196 | YES | 785
8 / 12:00 | 0.76 | 111 | 84.36 | 11.1 | 7.46 | 20.5164 | YES | 762
9 / 4:00 | 0.74 | 111 | 82.14 | 11.4 | 7.47 | 20.1429 | YES | 741
10 / 8:00 | 0.79 | 111 | 87.69 | 12 | 7.45 | 19.3441 | YES | 874
11 / 12:00 | 0.81 | 111 | 89.91 | 12 | 7.59 | 20.3537 | YES | 895
12 / 8:00 | 0.8 | 111 | 88.8 | 12.3 | 7.67 | 20.4997 | YES | 852
13 / 12:00 | 0.78 | 111 | 86.58 | 12.9 | 7.65 | 19.432 | YES | 832
14 / 8:00 | 0.76 | 111 | 84.36 | 13.3 | 7.73 | 19.4451 | YES | 849
15 / 8:00 | 0.77 | 111 | 85.47 | 13.5 | 7.58 | 18.1763 | YES | 846
16 / 8:00 | 0.76 | 111 | 84.36 | 13.7 | 7.55 | 17.7186 | YES | 817
17 / 8:00 | 0.75 | 111 | 83.25 | 13.8 | 7.4 | 16.6329 | YES | 839
18 / 12:00 | 0.74 | 111 | 82.14 | 13.8 | 7.4 | 16.614 | YES | 867
19 / 12:00 | 0.76 | 111 | 84.36 | 13.7 | 7.41 | 16.8252 | YES | 890
20 / 8:00 | 0.73 | 111 | 81.03 | 13.6 | 7.45 | 17.1314 | YES | 867
21 / 8:00 | 0.76 | 111 | 84.36 | 13.5 | 7.5 | 17.6273 | YES | 858
22 / 8:00 | 0.78 | 111 | 86.58 | 13.3 | 7.47 | 17.7066 | YES | 816
23 / 8:00 | 0.79 | 111 | 87.69 | 13.1 | 7.45 | 17.8319 | YES | 852
24 / 8:00 | 0.79 | 111 | 87.69 | 13 | 7.38 | 17.4927 | YES | 847
25 / 16:00 | 0.8 | 111 | 88.8 | 13 | 7.3 | 17.0024 | YES | 858
26 / 12:00 | 0.78 | 111 | 86.58 | 12.9 | 7.38 | 17.5894 | YES | 855
27 / 8:00 | 0.76 | 111 | 84.36 | 13.3 | 7.4 | 17.2154 | YES | 835
28 / 8:00 | 0.78 | 111 | 86.58 | 13.5 | 7.43 | 17.2163 | YES | 870
29 / 8:00 | 0.78 | 111 | 86.58 | 13.8 | 7.52 | 17.4467 | YES | 878
30 / 12:00 | 0.77 | 111 | 85.47 | 13.9 | 7.47 | 16.9944 | YES | 885
31 / 12:00 | 0.77 | 111 | 85.47 | 14.1 | 7.44 | 16.5846 | YES | 874
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | May | 999.99 | 999.99 | 999.99 | 0.051582 | 0.042553 | 999.99 | 12 | 0 | 0.051759 | 999.99 | 999.99 | 999.99 | 0.7352 | 0.72124 | 999.99 | 16 | 0.72124 | 0.72
2 | May | 999.99 | 999.99 | 999.99 | 0.072055 | 0.043966 | 999.99 | 12 | 0 | 0.072055 | 999.99 | 999.99 | 999.99 | 0.71842 | 0.76429 | 999.99 | 12 | 0.71842 | 0.72
3 | May | 999.99 | 999.99 | 0.11341 | 0.046537 | 0.048971 | 999.99 | 8 | 0 | 0.11428 | 999.99 | 999.99 | 0.76835 | 0.80121 | 0.82889 | 999.99 | 8 | 0.76835 | 0.77
4 | May | 999.99 | 999.99 | 0.093117 | 0.044712 | 0.044103 | 999.99 | 8 | 0 | 0.093608 | 999.99 | 999.99 | 0.81058 | 0.84161 | 0.86251 | 999.99 | 8 | 0.81058 | 0.81
5 | May | 999.99 | 999.99 | 0.060376 | 0.091783 | 999.99 | 999.99 | 12 | 0 | 0.091783 | 999.99 | 999.99 | 0.85345 | 0.86246 | 999.99 | 999.99 | 8 | 0.85345 | 0.85
6 | May | 999.99 | 999.99 | 0.078239 | 0.04744 | 999.99 | 999.99 | 8 | 0 | 0.078415 | 999.99 | 999.99 | 0.83743 | 0.85445 | 999.99 | 999.99 | 8 | 0.83743 | 0.84
7 | May | 999.99 | 999.99 | 0.055528 | 0.052799 | 999.99 | 999.99 | 8 | 0 | 0.057118 | 999.99 | 999.99 | 0.80333 | 0.80639 | 999.99 | 999.99 | 12 | 0.81 | 0.81
8 | May | 999.99 | 0.084363 | 0.057176 | 999.99 | 999.99 | 999.99 | 4 | 0 | 0.086954 | 999.99 | 0.76511 | 0.76829 | 999.99 | 999.99 | 999.99 | 12 | 0.76 | 0.76
9 | May | 999.99 | 0.07023 | 0.068895 | 999.99 | 0.057569 | 999.99 | 4 | 0 | 0.070819 | 999.99 | 0.74515 | 0.78154 | 999.99 | 0.78066 | 999.99 | 4 | 0.74515 | 0.75
10 | May | 999.99 | 999.99 | 0.076629 | 0.069032 | 0.071152 | 999.99 | 8 | 0 | 0.077669 | 999.99 | 999.99 | 0.78278 | 0.79786 | 0.81652 | 999.99 | 8 | 0.78278 | 0.78
11 | May | 999.99 | 999.99 | 0.13051 | 0.19764 | 999.99 | 999.99 | 12 | 0 | 0.19764 | 999.99 | 999.99 | 0.79786 | 0.81446 | 999.99 | 999.99 | 8 | 0.79786 | 0.8
12 | May | 999.99 | 999.99 | 0.11125 | 0.1003 | 999.99 | 999.99 | 8 | 0 | 0.11453 | 999.99 | 999.99 | 0.80427 | 0.83531 | 999.99 | 999.99 | 8 | 0.80427 | 0.8
13 | May | 999.99 | 999.99 | 0.11495 | 0.11275 | 0.11504 | 999.99 | 16 | 0 | 0.11887 | 999.99 | 999.99 | 0.77907 | 0.78478 | 0.78737 | 999.99 | 12 | 0.78 | 0.78
14 | May | 999.99 | 999.99 | 0.15126 | 0.38061 | 999.99 | 999.99 | 12 | 0 | 0.38061 | 999.99 | 999.99 | 0.76918 | 0.78266 | 999.99 | 999.99 | 8 | 0.76918 | 0.77
15 | May | 999.99 | 999.99 | 0.20155 | 0.18098 | 999.99 | 999.99 | 8 | 0 | 0.21492 | 999.99 | 999.99 | 0.78107 | 0.80598 | 999.99 | 999.99 | 8 | 0.78107 | 0.78
16 | May | 999.99 | 999.99 | 0.25282 | 0.04057 | 999.99 | 999.99 | 8 | 0 | 0.2541 | 999.99 | 999.99 | 0.75822 | 0.77477 | 999.99 | 999.99 | 8 | 0.75822 | 0.76
17 | May | 999.99 | 999.99 | 0.048677 | 0.033268 | 0.030167 | 999.99 | 8 | 0 | 0.05172 | 999.99 | 999.99 | 0.75269 | 0.75793 | 0.75675 | 999.99 | 8 | 0.75269 | 0.75
18 | May | 999.99 | 999.99 | 999.99 | 0.038058 | 0.034642 | 999.99 | 12 | 0 | 0.038117 | 999.99 | 999.99 | 999.99 | 0.74197 | 0.75793 | 999.99 | 12 | 0.74197 | 0.74
19 | May | 999.99 | 999.99 | 999.99 | 0.03794 | 999.99 | 999.99 | 12 | 0 | 0.038058 | 999.99 | 999.99 | 999.99 | 0.75245 | 999.99 | 999.99 | 12 | 0.75245 | 0.75
20 | May | 999.99 | 999.99 | 0.088073 | 0.035015 | 0.035467 | 999.99 | 8 | 0 | 0.088073 | 999.99 | 999.99 | 0.73973 | 0.76841 | 0.78873 | 999.99 | 8 | 0.73973 | 0.74
21 | May | 999.99 | 999.99 | 0.082302 | 0.035643 | 999.99 | 999.99 | 8 | 0 | 0.087818 | 999.99 | 999.99 | 0.77083 | 0.79409 | 999.99 | 999.99 | 8 | 0.77083 | 0.77
22 | May | 999.99 | 999.99 | 0.080928 | 0.037233 | 0.040668 | 999.99 | 8 | 0 | 0.087229 | 999.99 | 999.99 | 0.78107 | 0.7915 | 0.80186 | 999.99 | 8 | 0.78107 | 0.78
23 | May | 999.99 | 999.99 | 0.058531 | 0.03478 | 999.99 | 999.99 | 8 | 0 | 0.060572 | 999.99 | 999.99 | 0.78873 | 0.81405 | 999.99 | 999.99 | 8 | 0.78873 | 0.79
24 | May | 999.99 | 999.99 | 0.060396 | 0.037724 | 999.99 | 999.99 | 8 | 0 | 0.062633 | 999.99 | 999.99 | 0.78667 | 0.80339 | 999.99 | 999.99 | 8 | 0.78667 | 0.79
25 | May | 999.99 | 999.99 | 999.99 | 0.046518 | 0.043652 | 999.99 | 12 | 0 | 0.046773 | 999.99 | 999.99 | 999.99 | 0.80151 | 0.79933 | 999.99 | 16 | 0.79933 | 0.8
26 | May | 999.99 | 999.99 | 999.99 | 0.05488 | 999.99 | 999.99 | 12 | 0 | 0.056215 | 999.99 | 999.99 | 999.99 | 0.7826 | 999.99 | 999.99 | 12 | 0.7826 | 0.78
27 | May | 999.99 | 999.99 | 0.18869 | 0.060023 | 0.0538 | 999.99 | 8 | 0 | 0.18942 | 999.99 | 999.99 | 0.76093 | 0.78361 | 0.80333 | 999.99 | 8 | 0.76093 | 0.76
28 | May | 999.99 | 999.99 | 0.075392 | 0.06385 | 0.055979 | 999.99 | 8 | 0 | 0.079927 | 999.99 | 999.99 | 0.78096 | 0.79256 | 0.79515 | 999.99 | 8 | 0.78096 | 0.78
29 | May | 999.99 | 999.99 | 0.096925 | 999.99 | 0.070249 | 999.99 | 8 | 0 | 0.099732 | 999.99 | 999.99 | 0.7773 | 999.99 | 0.78785 | 999.99 | 8 | 0.7773 | 0.78
30 | May | 999.99 | 999.99 | 999.99 | 0.090291 | 0.082753 | 999.99 | 12 | 0 | 0.090683 | 999.99 | 999.99 | 999.99 | 0.77748 | 0.78337 | 999.99 | 12 | 0.77748 | 0.78
31 | May | 999.99 | 999.99 | 999.99 | 0.10028 | 0.094374 | 999.99 | 12 | 0 | 0.10028 | 999.99 | 999.99 | 999.99 | 0.77477 | 0.79102 | 999.99 | 12 | 0.77477 | 0.77