## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Jun_24
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
2 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
3 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
4 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
5 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
6 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
7 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
8 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
9 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
10 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
11 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
12 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
13 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
14 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
15 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
16 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
17 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
18 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
19 | OFF | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02
20 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
21 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
22 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
23 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
24 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
25 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
26 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
27 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
28 | OFF | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02
29 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
30 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Zachary J. Dues
[5 empty] | SIGNATURE: Zachary J. Dues |  |  | DATE:07/01/2024
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Jun_24 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 12:00 | 0.78 | 111 | 86.58 | 14.3 | 7.57 | 17.1906 | YES | 892
2 / 12:00 | 0.82 | 111 | 91.02 | 14.5 | 7.52 | 16.7285 | YES | 831
3 / 12:00 | 0.78 | 111 | 86.58 | 14.3 | 7.45 | 16.4445 | YES | 854
4 / 8:00 | 0.76 | 111 | 84.36 | 14.5 | 7.42 | 16.0112 | YES | 848
5 / 8:00 | 0.73 | 111 | 81.03 | 13.9 | 7.49 | 17.0429 | YES | 844
6 / 8:00 | 0.72 | 111 | 79.92 | 13.8 | 7.28 | 15.8562 | YES | 853
7 / 12:00 | 0.77 | 111 | 85.47 | 14.1 | 7.26 | 15.5155 | YES | 887
8 / 12:00 | 0.8 | 111 | 88.8 | 13.9 | 7.25 | 15.7194 | YES | 885
9 / 12:00 | 0.81 | 111 | 89.91 | 14 | 7.22 | 15.4599 | YES | 858
10 / 8:00 | 0.8 | 111 | 88.8 | 14.3 | 7.19 | 14.9688 | YES | 836
11 / 8:00 | 0.81 | 111 | 89.91 | 14.4 | 7.25 | 15.221 | YES | 868
12 / 12:00 | 0.79 | 111 | 87.69 | 14.4 | 7.35 | 15.7596 | YES | 849
13 / 8:00 | 0.74 | 111 | 82.14 | 14.6 | 7.41 | 15.81 | YES | 823
14 / 8:00 | 0.75 | 111 | 83.25 | 14.7 | 7.41 | 15.7228 | YES | 860
15 / 12:00 | 0.76 | 111 | 84.36 | 14.6 | 7.51 | 16.4435 | YES | 878
16 / 12:00 | 0.76 | 111 | 84.36 | 14.5 | 7.47 | 16.3102 | YES | 882
17 / 16:00 | 0.76 | 111 | 84.36 | 14.5 | 7.58 | 16.9875 | YES | 863
18 / 8:00 | 0.74 | 111 | 82.14 | 14.3 | 7.63 | 17.4963 | YES | 883
19 / 12:00 | 0.76 | 111 | 84.36 | 14.1 | 7.52 | 17.0631 | YES | 849
20 / 8:00 | 0.76 | 111 | 84.36 | 14.2 | 7.46 | 16.578 | YES | 823
21 / 8:00 | 0.75 | 111 | 83.25 | 14.3 | 7.41 | 16.1477 | YES | 837
22 / 12:00 | 0.78 | 111 | 86.58 | 14.7 | 7.39 | 15.6601 | YES | 873
23 / 8:00 | 0.75 | 111 | 83.25 | 15 | 7.35 | 15.0723 | YES | 890
24 / 12:00 | 0.76 | 111 | 84.36 | 15.6 | 7.36 | 14.5506 | YES | 853
25 / 8:00 | 0.72 | 111 | 79.92 | 16 | 7.35 | 14.0499 | YES | 878
26 / 8:00 | 0.72 | 111 | 79.92 | 16.4 | 7.54 | 14.6789 | YES | 859
27 / 8:00 | 0.77 | 111 | 85.47 | 16.3 | 7.46 | 14.4271 | YES | 802
28 / 12:00 | 0.78 | 111 | 86.58 | 16.4 | 7.41 | 14.0834 | YES | 837
29 / 8:00 | 0.77 | 111 | 85.47 | 16.4 | 7.42 | 14.1197 | YES | 847
30 / 12:00 | 0.76 | 111 | 84.36 | 16.3 | 7.47 | 14.4643 | YES | 819
31 |  | 111 |  |  |  |  | NO
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Jun | 999.99 | 999.99 | 999.99 | 0.11043 | 0.11326 | 999.99 | 16 | 0 | 0.11457 | 999.99 | 999.99 | 999.99 | 0.77683 | 0.79303 | 999.99 | 12 | 0.77683 | 0.78
2 | Jun | 999.99 | 999.99 | 999.99 | 0.1492 | 0.12342 | 999.99 | 12 | 0 | 0.1492 | 999.99 | 999.99 | 999.99 | 0.81782 | 0.82182 | 999.99 | 12 | 0.81782 | 0.82
3 | Jun | 999.99 | 999.99 | 999.99 | 0.031325 | 0.028891 | 999.99 | 12 | 0 | 0.033857 | 999.99 | 999.99 | 999.99 | 0.77536 | 0.78678 | 999.99 | 12 | 0.77536 | 0.78
4 | Jun | 999.99 | 999.99 | 0.068012 | 0.026633 | 999.99 | 999.99 | 8 | 0 | 0.069189 | 999.99 | 999.99 | 0.76129 | 0.78396 | 999.99 | 999.99 | 8 | 0.76129 | 0.76
5 | Jun | 999.99 | 999.99 | 0.058904 | 0.028577 | 999.99 | 999.99 | 8 | 0 | 0.058904 | 999.99 | 999.99 | 0.72872 | 0.74127 | 999.99 | 999.99 | 8 | 0.72872 | 0.73
6 | Jun | 999.99 | 999.99 | 0.051111 | 0.029303 | 0.031914 | 999.99 | 8 | 0 | 0.051916 | 999.99 | 999.99 | 0.72395 | 0.75416 | 0.77748 | 999.99 | 8 | 0.72395 | 0.72
7 | Jun | 999.99 | 999.99 | 999.99 | 0.036232 | 0.028263 | 999.99 | 12 | 0 | 0.036291 | 999.99 | 999.99 | 999.99 | 0.76694 | 0.79209 | 999.99 | 12 | 0.76694 | 0.77
8 | Jun | 999.99 | 999.99 | 999.99 | 0.029951 | 0.037528 | 999.99 | 16 | 0 | 0.04536 | 999.99 | 999.99 | 999.99 | 0.80039 | 0.80775 | 999.99 | 12 | 0.80039 | 0.8
9 | Jun | 999.99 | 999.99 | 999.99 | 0.039039 | 0.031678 | 999.99 | 12 | 0 | 0.039039 | 999.99 | 999.99 | 999.99 | 0.81016 | 0.83278 | 999.99 | 12 | 0.81016 | 0.81
10 | Jun | 999.99 | 999.99 | 0.093333 | 0.033131 | 0.025259 | 999.99 | 8 | 0 | 0.093333 | 999.99 | 999.99 | 0.80021 | 0.8313 | 0.84673 | 999.99 | 8 | 0.80021 | 0.8
11 | Jun | 999.99 | 999.99 | 0.053898 | 0.055626 | 0.02944 | 999.99 | 12 | 0 | 0.057392 | 999.99 | 999.99 | 0.80928 | 0.82424 | 0.81576 | 999.99 | 8 | 0.80928 | 0.81
12 | Jun | 999.99 | 999.99 | 0.040708 | 0.02997 | 999.99 | 999.99 | 8 | 0 | 0.042651 | 999.99 | 999.99 | 0.79373 | 0.7862 | 999.99 | 999.99 | 12 | 0.7862 | 0.79
13 | Jun | 999.99 | 999.99 | 0.082635 | 0.037685 | 0.03423 | 999.99 | 8 | 0 | 0.085815 | 999.99 | 999.99 | 0.75239 | 0.76771 | 0.78396 | 999.99 | 8 | 0.75239 | 0.75
14 | Jun | 999.99 | 999.99 | 0.068424 | 0.038352 | 0.034485 | 999.99 | 8 | 0 | 0.076001 | 999.99 | 999.99 | 0.75104 | 0.767 | 0.7723 | 999.99 | 8 | 0.75104 | 0.75
15 | Jun | 999.99 | 999.99 | 999.99 | 0.042769 | 999.99 | 999.99 | 12 | 0 | 0.043122 | 999.99 | 999.99 | 999.99 | 0.76511 | 999.99 | 999.99 | 12 | 0.76511 | 0.77
16 | Jun | 999.99 | 999.99 | 999.99 | 0.049521 | 0.048795 | 999.99 | 16 | 0 | 0.05278 | 999.99 | 999.99 | 999.99 | 0.76188 | 0.77094 | 999.99 | 12 | 0.76188 | 0.76
17 | Jun | 999.99 | 999.99 | 999.99 | 0.057491 | 0.063438 | 999.99 | 16 | 0 | 0.06387 | 999.99 | 999.99 | 999.99 | 0.76458 | 0.76241 | 999.99 | 16 | 0.76241 | 0.76
18 | Jun | 999.99 | 999.99 | 0.11279 | 0.063222 | 0.064773 | 0.05961 | 8 | 0 | 0.11279 | 999.99 | 999.99 | 0.74356 | 0.77348 | 0.77454 | 0.78366 | 8 | 0.74356 | 0.74
19 | Jun | 999.99 | 999.99 | 999.99 | 0.077237 | 0.071957 | 0.073665 | 12 | 0 | 0.078317 | 999.99 | 999.99 | 999.99 | 0.77018 | 0.7889 | 0.79167 | 12 | 0.77018 | 0.77
20 | Jun | 999.99 | 999.99 | 0.1035 | 0.084147 | 0.086679 | 999.99 | 8 | 0 | 0.1044 | 999.99 | 999.99 | 0.75781 | 0.78278 | 0.78054 | 999.99 | 8 | 0.75781 | 0.76
21 | Jun | 999.99 | 999.99 | 0.13426 | 0.10003 | 0.10749 | 0.10223 | 8 | 0 | 0.13742 | 999.99 | 999.99 | 0.74974 | 0.77707 | 0.76812 | 0.77872 | 8 | 0.74974 | 0.75
22 | Jun | 999.99 | 999.99 | 999.99 | 0.11502 | 0.11812 | 999.99 | 16 | 0 | 0.11838 | 999.99 | 999.99 | 999.99 | 0.77589 | 0.78302 | 999.99 | 12 | 0.77589 | 0.78
23 | Jun | 999.99 | 999.99 | 0.17395 | 0.13391 | 0.127 | 999.99 | 8 | 0 | 0.17395 | 999.99 | 999.99 | 0.74957 | 0.768 | 0.77454 | 999.99 | 8 | 0.74957 | 0.75
24 | Jun | 999.99 | 999.99 | 999.99 | 0.036841 | 0.032876 | 999.99 | 12 | 0 | 0.036841 | 999.99 | 999.99 | 999.99 | 0.75487 | 0.7733 | 999.99 | 12 | 0.75487 | 0.75
25 | Jun | 999.99 | 999.99 | 0.090664 | 0.038097 | 0.039177 | 999.99 | 8 | 0 | 0.090664 | 999.99 | 999.99 | 0.72095 | 0.75186 | 0.76087 | 999.99 | 8 | 0.72095 | 0.72
26 | Jun | 999.99 | 999.99 | 0.095198 | 0.040668 | 0.034976 | 999.99 | 8 | 0 | 0.095198 | 999.99 | 999.99 | 0.72472 | 0.77159 | 0.79273 | 999.99 | 8 | 0.72472 | 0.72
27 | Jun | 999.99 | 999.99 | 0.088348 | 0.036311 | 0.029872 | 999.99 | 8 | 0 | 0.08874 | 999.99 | 999.99 | 0.76135 | 0.80098 | 0.82212 | 999.99 | 8 | 0.76135 | 0.76
28 | Jun | 999.99 | 999.99 | 999.99 | 0.090232 | 0.041395 | 0.042062 | 12 | 0 | 0.090232 | 999.99 | 999.99 | 999.99 | 0.77831 | 0.78678 | 0.7968 | 12 | 0.77831 | 0.78
29 | Jun | 999.99 | 999.99 | 0.08083 | 0.03741 | 999.99 | 999.99 | 8 | 0 | 0.081399 | 999.99 | 999.99 | 0.77248 | 0.77831 | 999.99 | 999.99 | 8 | 0.77248 | 0.77
30 | Jun | 999.99 | 999.99 | 999.99 | 0.049443 | 0.042356 | 999.99 | 12 | 0 | 0.049462 | 999.99 | 999.99 | 999.99 | 0.7594 | 0.77819 | 999.99 | 12 | 0.7594 | 0.76