## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Aug_24
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
2 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
3 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
4 | OFF | OFF | OFF | 0.03 | 0.02 | OFF | 0.03
5 | OFF | OFF | 0.02 | 0.2 | OFF | OFF | 0.02
6 | OFF | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02
7 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
8 | OFF | OFF | 0.02 | 0.03 | 0.02 | OFF | 0.03
9 | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.02 | 0.03
10 | OFF | OFF | OFF | 0.03 | 0.03 | OFF | 0.03
11 | OFF | OFF | OFF | 0.03 | 0.02 | 0.02 | 0.03
12 | OFF | OFF | 0.02 | 0.03 | 0.02 | OFF | 0.03
13 | OFF | OFF | 0.02 | 0.03 | 0.02 | OFF | 0.03
14 | OFF | 0.02 | 0.02 | OFF | 0.02 | OFF | 0.02
15 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
16 | OFF | OFF | OFF | 0.03 | 0.02 | OFF | 0.03
17 | OFF | 0.02 | OFF | OFF | 0.03 | 0.02 | 0.03
18 | OFF | OFF | OFF | 0.03 | 0.02 | OFF | 0.03
19 | OFF | OFF | 0.02 | 0.03 | 0.02 | OFF | 0.03
20 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
21 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
22 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02 | 0.02
23 | OFF | OFF | 0.02 | 0.03 | OFF | OFF | 0.03
24 | OFF | 0.04 | 0.02 | OFF | 0.02 | 0.02 | 0.04
25 | OFF | OFF | 0.03 | 0.03 | 0.02 | OFF | 0.03
26 | OFF | OFF | OFF | 0.03 | OFF | OFF | 0.03
27 | 0.02 | OFF | 0.02 | 0.03 | 0.02 | OFF | 0.03
28 | OFF | OFF | 0.02 | OFF | OFF | 0.02 | 0.02
29 | 0.02 | OFF | 0.02 | 0.03 | OFF | OFF | 0.03
30 | 0.02 | 0.02 | OFF | 0.03 | 0.02 | OFF | 0.03
31 | OFF | OFF | OFF | 0.03 | 0.02 | OFF | 0.03
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:09/03/2024
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Aug_24 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 8:00 | 0.75 | 111 | 83.25 | 19.4 | 7.44 | 11.6058 | YES | 825
2 / 8:00 | 0.74 | 111 | 82.14 | 19.4 | 7.47 | 11.7231 | YES | 809
3 / 8:00 | 0.71 | 111 | 78.81 | 19.4 | 7.41 | 11.4237 | YES | 873
4 / 12:00 | 0.72 | 111 | 79.92 | 19.7 | 7.4 | 11.1663 | YES | 861
5 / 8:00 | 0.71 | 111 | 78.81 | 19.8 | 7.51 | 11.5439 | YES | 880
6 / 12:00 | 0.76 | 111 | 84.36 | 19.9 | 7.52 | 11.5757 | YES | 848
7 / 8:00 | 0.75 | 111 | 83.25 | 19.8 | 7.43 | 11.2553 | YES | 773
8 / 16:00 | 0.81 | 111 | 89.91 | 19.9 | 7.48 | 11.4696 | YES | 811
9 / 8:00 | 0.73 | 111 | 81.03 | 20.1 | 7.43 | 11.0047 | YES | 821
10 / 12:00 | 0.73 | 111 | 81.03 | 20 | 7.42 | 11.0377 | YES | 861
11 / 12:00 | 0.72 | 111 | 79.92 | 20 | 7.4 | 10.9428 | YES | 853
12 / 8:00 | 0.73 | 111 | 81.03 | 19.8 | 7.52 | 11.6137 | YES | 856
13 / 8:00 | 0.73 | 111 | 81.03 | 20 | 7.49 | 11.3306 | YES | 856
14 / 4:00 | 0.76 | 111 | 84.36 | 19.8 | 7.52 | 11.6538 | YES | 852
15 / 8:00 | 0.79 | 111 | 87.69 | 19.7 | 7.55 | 11.9056 | YES | 980
16 / 12:00 | 0.81 | 111 | 89.91 | 19.3 | 7.39 | 11.5472 | YES | 852
17 / 4:00 | 0.81 | 111 | 89.91 | 19.4 | 7.34 | 11.2573 | YES | 846
18 / 12:00 | 0.8 | 111 | 88.8 | 19.2 | 7.32 | 11.3119 | YES | 833
19 / 8:00 | 0.78 | 111 | 86.58 | 19.1 | 7.43 | 11.8389 | YES | 825
20 / 4:00 | 0.76 | 111 | 84.36 | 19.1 | 7.46 | 11.9448 | YES | 854
21 / 8:00 | 0.74 | 111 | 82.14 | 19.1 | 7.47 | 11.962 | YES | 890
22 / 20:00 | 0.76 | 111 | 84.36 | 19 | 7.51 | 12.2519 | YES | 883
23 / 8:00 | 0.76 | 111 | 84.36 | 18.9 | 7.49 | 12.2428 | YES | 909
24 / 4:00 | 0.74 | 111 | 82.14 | 18.7 | 7.41 | 12.0158 | YES | 892
25 / 8:00 | 0.74 | 111 | 82.14 | 18.5 | 7.38 | 12.0428 | YES | 822
26 / 12:00 | 0.79 | 111 | 87.69 | 18.5 | 7.42 | 12.2942 | YES | 861
27 / 8:00 | 0.79 | 111 | 87.69 | 18.5 | 7.41 | 12.2484 | YES | 856
28 / 8:00 | 0.77 | 111 | 85.47 | 18.4 | 7.48 | 12.628 | YES | 847
29 / 8:00 | 0.77 | 111 | 85.47 | 18.6 | 7.47 | 12.4133 | YES | 835
30 / 0:00 | 0.76 | 111 | 84.36 | 18.8 | 7.3 | 11.4811 | YES | 889
31 / 12:00 | 0.76 | 111 | 84.36 | 18.8 | 7.27 | 11.3531 | YES | 853
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Aug | 999.99 | 999.99 | 0.17911 | 0.16665 | 0.16694 | 999.99 | 8 | 0 | 0.17911 | 999.99 | 999.99 | 0.75027 | 0.78991 | 0.78708 | 999.99 | 8 | 0.75027 | 0.75
2 | Aug | 999.99 | 999.99 | 0.19615 | 0.055056 | 0.062496 | 999.99 | 8 | 0 | 0.19904 | 999.99 | 999.99 | 0.7405 | 0.77336 | 0.77047 | 999.99 | 8 | 0.7405 | 0.74
3 | Aug | 999.99 | 999.99 | 0.074843 | 0.070622 | 0.0644 | 0.063791 | 8 | 0 | 0.078062 | 999.99 | 999.99 | 0.70723 | 0.74951 | 0.75451 | 0.76235 | 8 | 0.70723 | 0.71
4 | Aug | 999.99 | 999.99 | 999.99 | 0.077846 | 0.074313 | 999.99 | 12 | 0 | 0.081085 | 999.99 | 999.99 | 999.99 | 0.71712 | 0.74963 | 999.99 | 12 | 0.71712 | 0.72
5 | Aug | 999.99 | 999.99 | 0.099222 | 0.082282 | 999.99 | 999.99 | 8 | 0 | 0.099242 | 999.99 | 999.99 | 0.70752 | 0.7551 | 999.99 | 999.99 | 8 | 0.70752 | 0.71
6 | Aug | 999.99 | 0.087543 | 999.99 | 0.090507 | 0.087641 | 999.99 | 16 | 0 | 0.091292 | 999.99 | 0.76111 | 999.99 | 0.75758 | 0.7796 | 999.99 | 12 | 0.75758 | 0.76
7 | Aug | 999.99 | 999.99 | 0.11371 | 0.1023 | 0.093549 | 0.10374 | 8 | 0 | 0.11915 | 999.99 | 999.99 | 0.75398 | 0.7985 | 0.82547 | 0.82017 | 8 | 0.75398 | 0.75
8 | Aug | 999.99 | 999.99 | 0.11298 | 0.092156 | 0.090899 | 999.99 | 8 | 0 | 0.11298 | 999.99 | 999.99 | 0.84202 | 0.824 | 0.81122 | 999.99 | 16 | 0.81122 | 0.81
9 | Aug | 999.99 | 999.99 | 0.11316 | 0.10904 | 0.11141 | 0.10711 | 8 | 0 | 0.11316 | 999.99 | 999.99 | 0.73538 | 0.7541 | 0.74627 | 0.77183 | 8 | 0.73538 | 0.74
10 | Aug | 999.99 | 999.99 | 999.99 | 0.12342 | 0.11612 | 999.99 | 12 | 0 | 0.12682 | 999.99 | 999.99 | 999.99 | 0.7259 | 0.76535 | 999.99 | 12 | 0.7259 | 0.73
11 | Aug | 999.99 | 999.99 | 999.99 | 0.12973 | 0.12539 | 0.12527 | 12 | 0 | 0.13092 | 999.99 | 999.99 | 999.99 | 0.72484 | 0.76882 | 0.7849 | 12 | 0.72484 | 0.72
12 | Aug | 999.99 | 999.99 | 0.16098 | 0.14095 | 0.13803 | 999.99 | 8 | 0 | 0.21164 | 999.99 | 999.99 | 0.73226 | 0.772 | 0.79002 | 999.99 | 8 | 0.73226 | 0.73
13 | Aug | 999.99 | 999.99 | 0.17042 | 0.15091 | 0.1489 | 999.99 | 8 | 0 | 0.17075 | 999.99 | 999.99 | 0.73673 | 0.76706 | 0.80392 | 999.99 | 8 | 0.73673 | 0.74
14 | Aug | 999.99 | 0.22271 | 0.17491 | 999.99 | 0.17746 | 999.99 | 4 | 0 | 0.22477 | 999.99 | 0.75027 | 0.79521 | 999.99 | 0.78832 | 999.99 | 4 | 0.75027 | 0.75
15 | Aug | 999.99 | 999.99 | 0.20037 | 0.18583 | 0.18779 | 0.19103 | 8 | 0 | 0.20135 | 999.99 | 999.99 | 0.79273 | 0.79638 | 0.79844 | 0.81964 | 8 | 0.79273 | 0.79
16 | Aug | 999.99 | 999.99 | 999.99 | 0.20915 | 0.2062 | 999.99 | 12 | 0 | 0.21028 | 999.99 | 999.99 | 999.99 | 0.80851 | 0.83331 | 999.99 | 12 | 0.80851 | 0.81
17 | Aug | 999.99 | 0.22491 | 999.99 | 999.99 | 0.22866 | 0.23125 | 20 | 0 | 0.23243 | 999.99 | 0.81164 | 999.99 | 999.99 | 0.83107 | 0.8518 | 4 | 0.81164 | 0.81
18 | Aug | 999.99 | 999.99 | 999.99 | 0.27113 | 0.25686 | 999.99 | 12 | 0 | 0.27243 | 999.99 | 999.99 | 999.99 | 0.80068 | 0.82029 | 999.99 | 12 | 0.80068 | 0.8
19 | Aug | 999.99 | 999.99 | 0.30456 | 0.038175 | 0.042926 | 999.99 | 8 | 0 | 0.30456 | 999.99 | 999.99 | 0.77866 | 0.79986 | 0.80104 | 999.99 | 8 | 0.77866 | 0.78
20 | Aug | 999.99 | 0.058766 | 0.045105 | 0.044378 | 999.99 | 0.038784 | 4 | 0 | 0.058766 | 999.99 | 0.75487 | 0.78837 | 0.7955 | 999.99 | 0.77789 | 4 | 0.75487 | 0.75
21 | Aug | 999.99 | 999.99 | 0.056097 | 0.045909 | 0.042533 | 999.99 | 8 | 0 | 0.057 | 999.99 | 999.99 | 0.73803 | 0.78425 | 0.8048 | 999.99 | 8 | 0.73803 | 0.74
22 | Aug | 999.99 | 0.065342 | 0.047107 | 999.99 | 999.99 | 0.047715 | 4 | 0 | 0.069366 | 999.99 | 0.75858 | 0.78608 | 999.99 | 999.99 | 0.76547 | 20 | 0.75858 | 0.76
23 | Aug | 999.99 | 999.99 | 0.087052 | 0.041179 | 999.99 | 999.99 | 8 | 0 | 0.087052 | 999.99 | 999.99 | 0.75781 | 0.78466 | 999.99 | 999.99 | 8 | 0.75781 | 0.76
24 | Aug | 999.99 | 0.076217 | 0.058001 | 999.99 | 0.046714 | 0.041571 | 4 | 0 | 0.077689 | 999.99 | 0.73614 | 0.77324 | 999.99 | 0.75463 | 0.79809 | 4 | 0.73614 | 0.74
25 | Aug | 999.99 | 999.99 | 0.1014 | 0.046891 | 0.038921 | 999.99 | 8 | 0 | 0.10158 | 999.99 | 999.99 | 0.73915 | 0.78031 | 0.8144 | 999.99 | 8 | 0.73915 | 0.74
26 | Aug | 999.99 | 999.99 | 999.99 | 0.04642 | 999.99 | 999.99 | 12 | 0 | 0.049658 | 999.99 | 999.99 | 999.99 | 0.79356 | 999.99 | 999.99 | 12 | 0.79356 | 0.79
27 | Aug | 0.047224 | 999.99 | 0.051935 | 0.042592 | 0.046184 | 999.99 | 8 | 0 | 0.051935 | 0.77707 | 999.99 | 0.78549 | 0.81252 | 0.8306 | 999.99 | 8 | 0.78549 | 0.79
28 | Aug | 999.99 | 999.99 | 0.058708 | 999.99 | 999.99 | 0.041257 | 8 | 0 | 0.059218 | 999.99 | 999.99 | 0.76935 | 999.99 | 999.99 | 0.79014 | 8 | 0.76935 | 0.77
29 | Aug | 0.045281 | 999.99 | 0.046675 | 0.04375 | 999.99 | 999.99 | 8 | 0 | 0.04907 | 0.80851 | 999.99 | 0.7753 | 0.80327 | 999.99 | 999.99 | 8 | 0.7753 | 0.78
30 | Aug | 0.059905 | 0.0485 | 999.99 | 0.046184 | 0.043358 | 999.99 | 4 | 0 | 0.04903 | 0.7604 | 0.78048 | 999.99 | 0.80068 | 0.81464 | 999.99 | 4 | 0.78048 | 0.78
31 | Aug | 999.99 | 999.99 | 999.99 | 0.055586 | 0.050345 | 999.99 | 12 | 0 | 0.058668 | 999.99 | 999.99 | 999.99 | 0.76323 | 0.78443 | 999.99 | 12 | 0.76323 | 0.76