## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Sep_24
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
2 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
3 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
4 | 0.02 | OFF | OFF | 0.04 | 0.02 | 0.02 | 0.04
5 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
6 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
7 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
8 | OFF | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02
9 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
10 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
11 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
12 | OFF | OFF | 0.02 | 0.05 | OFF | OFF | 0.05
13 | OFF | 0.03 | 0.03 | OFF | 0.03 | OFF | 0.03
14 | OFF | OFF | OFF | 0.03 | 0.03 | OFF | 0.03
15 | OFF | OFF | OFF | 0.03 | 0.03 | OFF | 0.03
16 | OFF | OFF | 0.03 | 0.03 | OFF | OFF | 0.03
17 | 0.02 | OFF | 0.02 | 0.03 | 0.02 | OFF | 0.03
18 | OFF | 0.02 | 0.02 | OFF | 0.02 | OFF | 0.02
19 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
20 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
21 | OFF | OFF | OFF | 0.02 | 0.029617 | OFF | 0.03
22 | OFF | OFF | OFF | 0.03 | 0.02 | 0.02 | 0.03
23 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
24 | OFF | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02
25 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
26 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
27 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
28 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
29 | OFF | OFF | OFF | 0.02 | 0.032817 | OFF | 0.03
30 | OFF | OFF | 0.03 | OFF | 0.03 | 0.02 | 0.03
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:10/01/2024
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Sep_24 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 12:00 | 0.75 | 111 | 83.25 | 18.8 | 7.37 | 11.7719 | YES | 858
2 / 12:00 | 0.75 | 111 | 83.25 | 18.8 | 7.44 | 12.0836 | YES | 848
3 / 8:00 | 0.72 | 111 | 79.92 | 18.8 | 7.54 | 12.4997 | YES | 887
4 / 0:00 | 0.76 | 111 | 84.36 | 18.8 | 7.48 | 12.2794 | YES | 832
5 / 12:00 | 0.8 | 111 | 88.8 | 19.1 | 7.46 | 11.9998 | YES | 829
6 / 8:00 | 0.77 | 111 | 85.47 | 19.1 | 7.41 | 11.7374 | YES | 813
7 / 12:00 | 0.75 | 111 | 83.25 | 19.2 | 7.35 | 11.3739 | YES | 810
8 / 12:00 | 0.77 | 111 | 85.47 | 19.2 | 7.32 | 11.2729 | YES | 868
9 / 8:00 | 0.75 | 111 | 83.25 | 19.3 | 7.46 | 11.7718 | YES | 873
10 / 12:00 | 0.76 | 111 | 84.36 | 19.3 | 7.48 | 11.8737 | YES | 849
11 / 8:00 | 0.78 | 111 | 86.58 | 19.4 | 7.48 | 11.8212 | YES | 863
12 / 8:00 | 0.81 | 111 | 89.91 | 19.3 | 7.47 | 11.8975 | YES | 902
13 / 4:00 | 0.78 | 111 | 86.58 | 19 | 7.36 | 11.6112 | YES | 848
14 / 12:00 | 0.75 | 111 | 83.25 | 19 | 7.3 | 11.3146 | YES | 826
15 / 12:00 | 0.74 | 111 | 82.14 | 18.8 | 7.29 | 11.412 | YES | 824
16 / 8:00 | 0.69 | 111 | 76.59 | 18.5 | 7.42 | 12.154 | YES | 810
17 / 8:00 | 0.72 | 111 | 79.92 | 18.3 | 7.45 | 12.4999 | YES | 891
18 / 4:00 | 0.73 | 111 | 81.03 | 18 | 7.49 | 12.9603 | YES | 878
19 / 8:00 | 0.75 | 111 | 83.25 | 17.8 | 7.41 | 12.7789 | YES | 857
20 / 8:00 | 0.8 | 111 | 88.8 | 17.5 | 7.23 | 12.2628 | YES | 870
21 / 12:00 | 0.81 | 111 | 89.91 | 17.3 | 7.18 | 12.2129 | YES | 822
22 / 12:00 | 0.82 | 111 | 91.02 | 17.3 | 7.28 | 12.6914 | YES | 826
23 / 8:00 | 0.79 | 111 | 87.69 | 17.2 | 7.4 | 13.3148 | YES | 846
24 / 16:00 | 0.79 | 111 | 87.69 | 17.2 | 7.41 | 13.3644 | YES | 833
25 / 8:00 | 0.75 | 111 | 83.25 | 17.3 | 7.45 | 13.4127 | YES | 860
26 / 8:00 | 0.75 | 111 | 83.25 | 17.2 | 7.47 | 13.6036 | YES | 852
27 / 8:00 | 0.74 | 111 | 82.14 | 17.4 | 7.34 | 12.7739 | YES | 883
28 / 8:00 | 0.73 | 111 | 81.03 | 17.2 | 7.32 | 12.8356 | YES | 874
29 / 12:00 | 0.75 | 111 | 83.25 | 17 | 7.33 | 13.0874 | YES | 834
30 / 8:00 | 0.74 | 111 | 82.14 | 16.8 | 7.47 | 13.9568 | YES | 849
31 |  | 111 |  |  |  |  | NO
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Sep | 999.99 | 999.99 | 999.99 | 0.06069 | 0.051111 | 999.99 | 12 | 0 | 0.061652 | 999.99 | 999.99 | 999.99 | 0.75375 | 0.80522 | 999.99 | 12 | 0.75375 | 0.75
2 | Sep | 999.99 | 999.99 | 999.99 | 0.064577 | 0.050051 | 999.99 | 12 | 0 | 0.065166 | 999.99 | 999.99 | 999.99 | 0.75422 | 0.77984 | 999.99 | 12 | 0.75422 | 0.75
3 | Sep | 999.99 | 999.99 | 0.077767 | 0.056529 | 999.99 | 999.99 | 8 | 0 | 0.077767 | 999.99 | 999.99 | 0.72537 | 0.76241 | 999.99 | 999.99 | 8 | 0.72537 | 0.73
4 | Sep | 0.047382 | 999.99 | 999.99 | 0.05645 | 0.045968 | 0.043691 | 12 | 0 | 0.06071 | 0.76029 | 999.99 | 999.99 | 0.78702 | 0.80386 | 0.82724 | 0 | 0.76 | 0.76
5 | Sep | 999.99 | 999.99 | 999.99 | 0.055253 | 0.052073 | 999.99 | 12 | 0 | 0.055449 | 999.99 | 999.99 | 999.99 | 0.79738 | 0.83066 | 999.99 | 12 | 0.79738 | 0.8
6 | Sep | 999.99 | 999.99 | 0.066147 | 999.99 | 0.051033 | 999.99 | 8 | 0 | 0.066579 | 999.99 | 999.99 | 0.77495 | 999.99 | 0.7988 | 999.99 | 8 | 0.77495 | 0.77
7 | Sep | 999.99 | 999.99 | 999.99 | 0.061672 | 0.053879 | 999.99 | 12 | 0 | 0.061907 | 999.99 | 999.99 | 999.99 | 0.75257 | 0.80174 | 999.99 | 12 | 0.75257 | 0.75
8 | Sep | 999.99 | 999.99 | 999.99 | 0.067403 | 0.057137 | 0.05278 | 12 | 0 | 0.067403 | 999.99 | 999.99 | 999.99 | 0.76647 | 0.80628 | 0.82123 | 12 | 0.76647 | 0.77
9 | Sep | 999.99 | 999.99 | 0.08452 | 0.0644 | 0.060533 | 0.062064 | 8 | 0 | 0.088367 | 999.99 | 999.99 | 0.76447 | 0.78814 | 0.8081 | 0.82742 | 8 | 0.76447 | 0.76
10 | Sep | 999.99 | 999.99 | 999.99 | 0.078199 | 0.065342 | 999.99 | 12 | 0 | 0.079809 | 999.99 | 999.99 | 999.99 | 0.76146 | 0.80274 | 999.99 | 12 | 0.76146 | 0.76
11 | Sep | 999.99 | 999.99 | 0.084952 | 0.069562 | 0.067835 | 999.99 | 8 | 0 | 0.084952 | 999.99 | 999.99 | 0.77395 | 0.83054 | 0.85586 | 999.99 | 8 | 0.77395 | 0.77
12 | Sep | 999.99 | 999.99 | 0.091684 | 0.11114 | 999.99 | 999.99 | 12 | 0 | 0.11114 | 999.99 | 999.99 | 0.81063 | 0.84738 | 999.99 | 999.99 | 8 | 0.81063 | 0.81
13 | Sep | 999.99 | 0.092862 | 0.08344 | 999.99 | 0.080457 | 999.99 | 4 | 0 | 0.096003 | 999.99 | 0.77607 | 0.80716 | 999.99 | 0.77895 | 999.99 | 4 | 0.77607 | 0.78
14 | Sep | 999.99 | 999.99 | 999.99 | 0.10083 | 0.086973 | 999.99 | 12 | 0 | 0.10442 | 999.99 | 999.99 | 999.99 | 0.75186 | 0.78166 | 999.99 | 12 | 0.75186 | 0.75
15 | Sep | 999.99 | 999.99 | 999.99 | 0.11496 | 0.098535 | 999.99 | 12 | 0 | 0.11496 | 999.99 | 999.99 | 999.99 | 0.73932 | 0.75398 | 999.99 | 12 | 0.73932 | 0.74
16 | Sep | 999.99 | 999.99 | 0.13628 | 0.11575 | 999.99 | 999.99 | 8 | 0 | 0.13628 | 999.99 | 999.99 | 0.69421 | 0.75192 | 999.99 | 999.99 | 8 | 0.69421 | 0.69
17 | Sep | 0.11854 | 999.99 | 0.11422 | 0.12452 | 0.1161 | 999.99 | 12 | 0 | 0.12547 | 0.71259 | 999.99 | 0.73343 | 0.77053 | 0.8031 | 999.99 | 8 | 0.73343 | 0.73
18 | Sep | 999.99 | 0.14604 | 0.12664 | 999.99 | 0.13844 | 999.99 | 4 | 0 | 0.15603 | 999.99 | 0.7322 | 0.77312 | 999.99 | 0.78178 | 999.99 | 4 | 0.7322 | 0.73
19 | Sep | 999.99 | 999.99 | 0.17438 | 0.14194 | 0.027909 | 999.99 | 8 | 0 | 0.17438 | 999.99 | 999.99 | 0.74863 | 0.81452 | 0.84514 | 999.99 | 8 | 0.74863 | 0.75
20 | Sep | 999.99 | 999.99 | 0.079357 | 999.99 | 0.037017 | 999.99 | 8 | 0 | 0.079357 | 999.99 | 999.99 | 0.80427 | 999.99 | 0.81546 | 999.99 | 8 | 0.80427 | 0.8
21 | Sep | 999.99 | 999.99 | 999.99 | 0.056588 | 0.029617 | 999.99 | 12 | 0 | 0.057687 | 999.99 | 999.99 | 999.99 | 0.80828 | 0.84974 | 999.99 | 12 | 0.80828 | 0.81
22 | Sep | 999.99 | 999.99 | 999.99 | 0.039235 | 0.032149 | 0.033072 | 12 | 0 | 0.043024 | 999.99 | 999.99 | 999.99 | 0.82241 | 0.84396 | 0.8558 | 12 | 0.82241 | 0.82
23 | Sep | 999.99 | 999.99 | 0.049914 | 0.033641 | 0.02893 | 999.99 | 8 | 0 | 0.053329 | 999.99 | 999.99 | 0.79073 | 0.81164 | 0.83466 | 999.99 | 8 | 0.79073 | 0.79
24 | Sep | 999.99 | 999.99 | 0.04216 | 999.99 | 0.031502 | 0.034996 | 8 | 0 | 0.045752 | 999.99 | 999.99 | 0.77719 | 999.99 | 0.78832 | 0.80557 | 16 | 0.79 | 0.79
25 | Sep | 999.99 | 999.99 | 0.039942 | 0.03421 | 0.032895 | 999.99 | 8 | 0 | 0.041139 | 999.99 | 999.99 | 0.74939 | 0.78443 | 0.80333 | 999.99 | 8 | 0.74939 | 0.75
26 | Sep | 999.99 | 999.99 | 0.033621 | 999.99 | 0.032542 | 999.99 | 8 | 0 | 0.037704 | 999.99 | 999.99 | 0.75758 | 999.99 | 0.76771 | 999.99 | 8 | 0.75758 | 0.76
27 | Sep | 999.99 | 999.99 | 0.073155 | 0.043475 | 0.030049 | 999.99 | 8 | 0 | 0.07337 | 999.99 | 999.99 | 0.73885 | 0.76818 | 0.80221 | 999.99 | 8 | 0.73885 | 0.74
28 | Sep | 999.99 | 999.99 | 0.087543 | 999.99 | 0.038077 | 999.99 | 8 | 0 | 0.092391 | 999.99 | 999.99 | 0.72896 | 999.99 | 0.76241 | 999.99 | 8 | 0.72896 | 0.73
29 | Sep | 999.99 | 999.99 | 999.99 | 0.052819 | 0.032817 | 999.99 | 12 | 0 | 0.05329 | 999.99 | 999.99 | 999.99 | 0.76223 | 0.79774 | 999.99 | 12 | 0.76223 | 0.76
30 | Sep | 999.99 | 999.99 | 0.051052 | 999.99 | 0.036193 | 0.036389 | 8 | 0 | 0.05488 | 999.99 | 999.99 | 0.75022 | 999.99 | 0.77442 | 0.7965 | 8 | 0.75022 | 0.75