## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Dec_24
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | 0.01 | 0.01 | OFF | 0.01
2 | OFF | OFF | 0.01 | 0.01 | OFF | OFF | 0.01
3 | 0.01 | OFF | 0.01 | 0.01 | 0.01 | OFF | 0.01
4 | OFF | OFF | 0.01 | OFF | 0.016858 | OFF | 0.02
5 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
6 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
7 | OFF | OFF | OFF | 0.02 | 0.024298 | OFF | 0.02
8 | OFF | OFF | OFF | 0.02 | 0.01 | OFF | 0.02
9 | OFF | OFF | 0.02 | 0.01 | 0.01 | OFF | 0.02
10 | OFF | OFF | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
11 | OFF | OFF | 0.01 | 0.01 | 0.017545 | OFF | 0.02
12 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
13 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
14 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
15 | OFF | OFF | OFF | 0.02 | 0.01 | 0.01 | 0.02
16 | OFF | OFF | OFF | 0.01 | 0.01 | 0.01 | 0.01
17 | OFF | OFF | OFF | 0.01 | 0.01 | OFF | 0.01
18 | OFF | OFF | 0.01 | 0.02 | 0.02 | OFF | 0.02
19 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
20 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
21 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
22 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
23 | OFF | OFF | 0.01 | 0.01 | 0.02 | OFF | 0.02
24 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
25 | OFF | OFF | 0.01 | OFF | 0.01 | OFF | 0.01
26 | OFF | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02
27 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
28 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
29 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
30 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
31 | OFF | OFF | 0.02 | 0.03 | 0.02 | OFF | 0.03
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:01/06/2025
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Dec_24 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 16:00 | 0.81 | 111 | 89.91 | 9.8 | 7.58 | 23.4474 | YES | 875
2 / 8:00 | 0.79 | 111 | 87.69 | 9.5 | 7.67 | 24.64 | YES | 890
3 / 8:00 | 0.8 | 111 | 88.8 | 9.5 | 7.72 | 25.111 | YES | 891
4 / 8:00 | 0.81 | 111 | 89.91 | 9.4 | 7.56 | 23.9092 | YES | 882
5 / 12:00 | 0.8 | 111 | 88.8 | 9 | 7.48 | 23.8402 | YES | 833
6 / 8:00 | 0.78 | 111 | 86.58 | 8.8 | 7.48 | 24.1046 | YES | 816
7 / 12:00 | 0.78 | 111 | 86.58 | 8.8 | 7.49 | 24.1903 | YES | 870
8 / 12:00 | 0.78 | 111 | 86.58 | 8.8 | 7.51 | 24.3627 | YES | 864
9 / 8:00 | 0.79 | 111 | 87.69 | 8.6 | 7.5 | 24.6303 | YES | 873
10 / 12:00 | 0.77 | 111 | 85.47 | 8.8 | 7.43 | 23.6542 | YES | 818
11 / 12:00 | 0.79 | 111 | 87.69 | 8.8 | 7.34 | 22.9653 | YES | 808
12 / 8:00 | 0.76 | 111 | 84.36 | 8.9 | 7.37 | 22.9783 | YES | 794
13 / 8:00 | 0.79 | 111 | 87.69 | 8.9 | 7.3 | 22.4942 | YES | 818
14 / 8:00 | 0.78 | 111 | 86.58 | 8.7 | 7.24 | 22.2917 | YES | 757
15 / 16:00 | 0.79 | 111 | 87.69 | 8.7 | 7.19 | 21.9278 | YES | 849
16 / 16:00 | 0.78 | 111 | 86.58 | 8.7 | 7.37 | 23.338 | YES | 825
17 / 12:00 | 0.75 | 111 | 83.25 | 8.8 | 7.37 | 23.1049 | YES | 835
18 / 8:00 | 0.75 | 111 | 83.25 | 8.8 | 7.29 | 22.4618 | YES | 803
19 / 8:00 | 0.77 | 111 | 85.47 | 9 | 7.21 | 21.6013 | YES | 800
20 / 8:00 | 0.75 | 111 | 83.25 | 9.1 | 7.16 | 21.0397 | YES | 790
21 / 12:00 | 0.74 | 111 | 82.14 | 9.2 | 7.1 | 20.4459 | YES | 790
22 / 12:00 | 0.73 | 111 | 81.03 | 9.1 | 7.07 | 20.3432 | YES | 839
23 / 8:00 | 0.73 | 111 | 81.03 | 9 | 7.2 | 21.4289 | YES | 829
24 / 8:00 | 0.72 | 111 | 79.92 | 9 | 7.21 | 21.48 | YES | 851
25 / 8:00 | 0.74 | 111 | 82.14 | 9 | 7.1 | 20.7154 | YES | 868
26 / 12:00 | 0.74 | 111 | 82.14 | 9.1 | 7.09 | 20.5085 | YES | 813
27 / 16:00 | 0.77 | 111 | 85.47 | 9.1 | 7.12 | 20.7942 | YES | 798
28 / 12:00 | 0.74 | 111 | 82.14 | 9.1 | 7.05 | 20.2246 | YES | 807
29 / 12:00 | 0.73 | 111 | 81.03 | 9.3 | 7.02 | 19.7331 | YES | 799
30 / 12:00 | 0.71 | 111 | 78.81 | 9.3 | 7.19 | 20.8903 | YES | 799
31 / 8:00 | 0.73 | 111 | 81.03 | 9.2 | 7.16 | 20.8552 | YES | 824
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Dec | 999.99 | 999.99 | 999.99 | 0.038195 | 0.021177 | 999.99 | 12 | 0 | 0.041257 | 999.99 | 999.99 | 999.99 | 0.80439 | 0.8127 | 999.99 | 16 | 0.81 | 0.81
2 | Dec | 999.99 | 999.99 | 0.070779 | 0.038391 | 999.99 | 999.99 | 8 | 0 | 0.071349 | 999.99 | 999.99 | 0.79768 | 0.81593 | 999.99 | 999.99 | 8 | 0.79768 | 0.8
3 | Dec | 0.052878 | 999.99 | 0.03531 | 0.018193 | 0.027811 | 999.99 | 0 | 0 | 0.056666 | 0.80545 | 999.99 | 0.79921 | 0.81646 | 0.82371 | 999.99 | 8 | 0.79921 | 0.8
4 | Dec | 999.99 | 999.99 | 0.037881 | 999.99 | 0.016858 | 999.99 | 8 | 0 | 0.038313 | 999.99 | 999.99 | 0.81205 | 999.99 | 0.81275 | 999.99 | 8 | 0.81205 | 0.81
5 | Dec | 999.99 | 999.99 | 0.034348 | 0.026476 | 0.025417 | 999.99 | 8 | 0 | 0.037822 | 999.99 | 999.99 | 0.80039 | 0.79927 | 0.79939 | 999.99 | 12 | 0.79927 | 0.8
6 | Dec | 999.99 | 999.99 | 0.069935 | 0.033111 | 0.027929 | 999.99 | 8 | 0 | 0.069955 | 999.99 | 999.99 | 0.77942 | 0.78661 | 0.78696 | 999.99 | 8 | 0.77942 | 0.78
7 | Dec | 999.99 | 999.99 | 999.99 | 0.033406 | 0.024298 | 999.99 | 12 | 0 | 0.034308 | 999.99 | 999.99 | 999.99 | 0.78072 | 0.79209 | 999.99 | 12 | 0.78072 | 0.78
8 | Dec | 999.99 | 999.99 | 999.99 | 0.033798 | 0.0189 | 999.99 | 12 | 0 | 0.033818 | 999.99 | 999.99 | 999.99 | 0.78096 | 0.80834 | 999.99 | 12 | 0.78096 | 0.78
9 | Dec | 999.99 | 999.99 | 0.045105 | 0.034701 | 0.019606 | 999.99 | 8 | 0 | 0.045477 | 999.99 | 999.99 | 0.78737 | 0.79568 | 0.80245 | 999.99 | 8 | 0.78737 | 0.79
10 | Dec | 999.99 | 999.99 | 0.029499 | 0.029342 | 0.01992 | 0.026261 | 8 | 0 | 0.033386 | 999.99 | 999.99 | 0.77995 | 0.77342 | 0.82029 | 0.82854 | 12 | 0.77342 | 0.77
11 | Dec | 999.99 | 999.99 | 0.040315 | 0.029774 | 0.017545 | 999.99 | 8 | 0 | 0.042612 | 999.99 | 999.99 | 0.80245 | 0.78696 | 0.80109 | 999.99 | 12 | 0.78696 | 0.79
12 | Dec | 999.99 | 999.99 | 0.044162 | 0.028282 | 0.028773 | 999.99 | 8 | 0 | 0.047911 | 999.99 | 999.99 | 0.76435 | 0.78319 | 0.79809 | 999.99 | 8 | 0.76435 | 0.76
13 | Dec | 999.99 | 999.99 | 0.048206 | 0.036841 | 0.033464 | 999.99 | 8 | 0 | 0.051896 | 999.99 | 999.99 | 0.78849 | 0.79397 | 0.81022 | 999.99 | 8 | 0.78849 | 0.79
14 | Dec | 999.99 | 999.99 | 0.064086 | 0.037312 | 0.035761 | 999.99 | 8 | 0 | 0.065872 | 999.99 | 999.99 | 0.77842 | 0.79179 | 0.8038 | 999.99 | 8 | 0.77842 | 0.78
15 | Dec | 999.99 | 999.99 | 999.99 | 0.045222 | 0.036448 | 0.036389 | 12 | 0 | 0.049266 | 999.99 | 999.99 | 999.99 | 0.7819 | 0.79986 | 0.81393 | 16 | 0.79 | 0.79
16 | Dec | 999.99 | 999.99 | 999.99 | 0.050699 | 0.042317 | 0.052505 | 20 | 0 | 0.054664 | 999.99 | 999.99 | 999.99 | 0.77495 | 0.78514 | 0.78414 | 16 | 0.78 | 0.78
17 | Dec | 999.99 | 999.99 | 999.99 | 0.048441 | 0.053447 | 999.99 | 16 | 0 | 0.055861 | 999.99 | 999.99 | 999.99 | 0.75016 | 0.75475 | 999.99 | 12 | 0.75016 | 0.75
18 | Dec | 999.99 | 999.99 | 0.066324 | 0.0517 | 0.048913 | 999.99 | 8 | 0 | 0.069955 | 999.99 | 999.99 | 0.75334 | 0.79668 | 0.79579 | 999.99 | 8 | 0.75334 | 0.75
19 | Dec | 999.99 | 999.99 | 0.065754 | 0.056489 | 0.054232 | 999.99 | 8 | 0 | 0.069032 | 999.99 | 999.99 | 0.77436 | 0.79326 | 0.78796 | 999.99 | 8 | 0.77436 | 0.77
20 | Dec | 999.99 | 999.99 | 0.071938 | 0.064145 | 0.063065 | 999.99 | 8 | 0 | 0.074215 | 999.99 | 999.99 | 0.75357 | 0.75422 | 0.7544 | 999.99 | 8 | 0.75357 | 0.75
21 | Dec | 999.99 | 999.99 | 0.11308 | 0.074803 | 0.068817 | 999.99 | 8 | 0 | 0.11553 | 999.99 | 999.99 | 0.74032 | 0.73803 | 0.75175 | 999.99 | 12 | 0.73803 | 0.74
22 | Dec | 999.99 | 999.99 | 999.99 | 0.086679 | 0.074313 | 999.99 | 12 | 0 | 0.087543 | 999.99 | 999.99 | 999.99 | 0.7339 | 0.76082 | 999.99 | 12 | 0.7339 | 0.73
23 | Dec | 999.99 | 999.99 | 0.10833 | 0.089525 | 0.086188 | 999.99 | 8 | 0 | 0.10984 | 999.99 | 999.99 | 0.72878 | 0.74032 | 0.74203 | 999.99 | 8 | 0.72878 | 0.73
24 | Dec | 999.99 | 999.99 | 0.11677 | 0.090939 | 0.096749 | 999.99 | 8 | 0 | 0.11734 | 999.99 | 999.99 | 0.71294 | 0.73832 | 0.74132 | 999.99 | 8 | 0.71294 | 0.71
25 | Dec | 999.99 | 999.99 | 0.12643 | 999.99 | 0.10409 | 999.99 | 8 | 0 | 0.12643 | 999.99 | 999.99 | 0.73597 | 999.99 | 0.73803 | 999.99 | 8 | 0.73597 | 0.74
26 | Dec | 999.99 | 999.99 | 999.99 | 0.11322 | 0.10584 | 0.10425 | 12 | 0 | 0.11581 | 999.99 | 999.99 | 999.99 | 0.7362 | 0.78484 | 0.7912 | 12 | 0.7362 | 0.74
27 | Dec | 999.99 | 999.99 | 999.99 | 0.12211 | 0.11812 | 999.99 | 12 | 0 | 0.12388 | 999.99 | 999.99 | 999.99 | 0.77748 | 0.77471 | 999.99 | 16 | 0.77471 | 0.77
28 | Dec | 999.99 | 999.99 | 999.99 | 0.1372 | 0.12984 | 999.99 | 12 | 0 | 0.13834 | 999.99 | 999.99 | 999.99 | 0.74127 | 0.7607 | 999.99 | 12 | 0.74127 | 0.74
29 | Dec | 999.99 | 999.99 | 999.99 | 0.14985 | 0.13854 | 999.99 | 12 | 0 | 0.1522 | 999.99 | 999.99 | 999.99 | 0.73226 | 0.7362 | 999.99 | 12 | 0.73226 | 0.73
30 | Dec | 999.99 | 999.99 | 999.99 | 0.15577 | 0.14928 | 999.99 | 12 | 0 | 0.15689 | 999.99 | 999.99 | 999.99 | 0.71259 | 0.74409 | 999.99 | 12 | 0.71259 | 0.71
31 | Dec | 999.99 | 999.99 | 0.18463 | 0.16082 | 0.15931 | 999.99 | 8 | 0 | 0.18891 | 999.99 | 999.99 | 0.72537 | 0.73326 | 0.76441 | 999.99 | 8 | 0.72537 | 0.73