## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Jan_25
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | All Cl2 residual at entry point ≥ 0.2 mg/l?
1 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
2 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
3 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
4 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
5 | OFF | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02
6 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
7 | 0.02 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
8 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
9 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
10 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
11 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
12 | OFF | OFF | OFF | 0.01 | 0.01 | OFF | 0.01
13 | OFF | OFF | 0.02 | 0.01 | 0.01 | 0.01 | 0.01
14 | OFF | OFF | 0.01 | 0.02 | 0.02 | 0.02 | 0.02
15 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
16 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
17 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
18 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
19 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
20 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
21 | OFF | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02
22 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
23 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
24 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
25 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
26 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
27 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
28 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
29 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
30 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
31 | OFF | OFF | 0.02 | 0.02 | 0.02312 | OFF | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:02/03/2025
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Jan_25 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 12:00 | 0.73 | 111 | 81.03 | 9 | 7.03 | 20.1933 | YES | 839
2 / 12:00 | 0.7 | 111 | 77.7 | 9.1 | 7.06 | 20.2045 | YES | 817
3 / 12:00 | 0.74 | 111 | 82.14 | 9.3 | 7.01 | 19.6866 | YES | 838
4 / 12:00 | 0.75 | 111 | 83.25 | 9.2 | 7.01 | 19.8375 | YES | 815
5 / 12:00 | 0.74 | 111 | 82.14 | 9.1 | 7 | 19.8758 | YES | 811
6 / 12:00 | 0.74 | 111 | 82.14 | 9.4 | 7.09 | 20.1101 | YES | 778
7 / 0:00 | 0.71 | 111 | 78.81 | 9.2 | 7.18 | 20.9544 | YES | 782
8 / 8:00 | 0.75 | 111 | 83.25 | 9.1 | 7.12 | 20.7476 | YES | 823
9 / 4:00 | 0.76 | 111 | 84.36 | 9.1 | 7 | 19.9203 | YES | 831
10 / 16:00 | 0.76 | 111 | 84.36 | 9.1 | 7 | 19.9203 | YES | 832
11 / 12:00 | 0.75 | 111 | 83.25 | 9.2 | 7 | 19.7687 | YES | 812
12 / 12:00 | 0.81 | 111 | 89.91 | 9.2 | 7.04 | 20.1804 | YES | 811
13 / 16:00 | 0.82 | 111 | 91.02 | 9.1 | 6.92 | 19.5047 | YES | 848
14 / 8:00 | 0.86 | 111 | 95.46 | 9.1 | 6.96 | 19.8659 | YES | 784
15 / 12:00 | 1.04 | 111 | 115.44 | 9.1 | 7.19 | 21.9685 | YES | 755
16 / 8:00 | 1.07 | 111 | 118.77 | 9.2 | 7.18 | 21.8214 | YES | 780
17 / 12:00 | 1.07 | 111 | 118.77 | 9.1 | 7.3 | 22.9141 | YES | 818
18 / 16:00 | 1.06 | 111 | 117.66 | 8.8 | 7.35 | 23.7649 | YES | 838
19 / 16:00 | 1.02 | 111 | 113.22 | 8.7 | 7.42 | 24.4137 | YES | 838
20 / 12:00 | 1 | 111 | 111 | 8.5 | 7.57 | 26.041 | YES | 797
21 / 20:00 | 0.98 | 111 | 108.78 | 8.3 | 7.55 | 26.1446 | YES | 806
22 / 20:00 | 0.91 | 111 | 101.01 | 8.1 | 7.65 | 27.2441 | YES | 7.66
23 / 16:00 | 0.86 | 111 | 95.46 | 7.7 | 7.44 | 25.8108 | YES | 744
24 / 16:00 | 0.84 | 111 | 93.24 | 7.6 | 7.39 | 25.4662 | YES | 792
25 / 16:00 | 0.82 | 111 | 91.02 | 7.7 | 7.33 | 24.7052 | YES | 809
26 / 12:00 | 0.82 | 111 | 91.02 | 7.3 | 7.24 | 24.5743 | YES | 799
27 / 8:00 | 0.82 | 111 | 91.02 | 7.2 | 7.39 | 26.098 | YES | 836
28 / 12:00 | 0.83 | 111 | 92.13 | 7.4 | 7.44 | 26.2447 | YES | 822
29 / 16:00 | 0.81 | 111 | 89.91 | 7.3 | 7.37 | 25.7096 | YES | 823
30 / 8:00 | 0.8 | 111 | 88.8 | 7.1 | 7.41 | 26.4016 | YES | 746
31 / 16:00 | 0.8 | 111 | 88.8 | 7.2 | 7.33 | 25.4863 | YES | 795
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Jan | 999.99 | 999.99 | 999.99 | 0.17336 | 0.16963 | 999.99 | 12 | 0 | 0.17407 | 999.99 | 999.99 | 999.99 | 0.72643 | 0.72796 | 999.99 | 12 | 0.72643 | 0.73
2 | Jan | 999.99 | 999.99 | 999.99 | 0.19415 | 0.1811 | 999.99 | 12 | 0 | 0.19501 | 999.99 | 999.99 | 999.99 | 0.69998 | 0.73261 | 999.99 | 12 | 0.69998 | 0.7
3 | Jan | 999.99 | 999.99 | 999.99 | 0.19902 | 0.19425 | 999.99 | 12 | 0 | 0.20206 | 999.99 | 999.99 | 999.99 | 0.74009 | 0.77342 | 999.99 | 12 | 0.74009 | 0.74
4 | Jan | 999.99 | 999.99 | 999.99 | 0.21407 | 0.20508 | 999.99 | 12 | 0 | 0.21407 | 999.99 | 999.99 | 999.99 | 0.74927 | 0.7614 | 999.99 | 12 | 0.74927 | 0.75
5 | Jan | 999.99 | 999.99 | 999.99 | 0.22177 | 0.21258 | 0.21507 | 12 | 0 | 0.22314 | 999.99 | 999.99 | 999.99 | 0.74115 | 0.78885 | 0.77 | 12 | 0.74115 | 0.74
6 | Jan | 999.99 | 999.99 | 999.99 | 0.23354 | 999.99 | 999.99 | 12 | 0 | 0.23354 | 999.99 | 999.99 | 999.99 | 0.73655 | 999.99 | 999.99 | 12 | 0.73655 | 0.74
7 | Jan | 0.24734 | 999.99 | 999.99 | 0.24022 | 0.2411 | 999.99 | 16 | 0 | 0.2443 | 0.70899 | 999.99 | 999.99 | 0.73561 | 0.75292 | 999.99 | 0 | 0.709 | 0.71
8 | Jan | 999.99 | 999.99 | 0.26193 | 0.25196 | 0.047892 | 999.99 | 8 | 0 | 0.26193 | 999.99 | 999.99 | 0.75139 | 0.76323 | 0.77318 | 999.99 | 8 | 0.75139 | 0.75
9 | Jan | 999.99 | 0.07021 | 0.052289 | 0.053702 | 0.04801 | 999.99 | 4 | 0 | 0.070564 | 999.99 | 0.75781 | 0.77436 | 0.82047 | 0.81305 | 999.99 | 4 | 0.75781 | 0.76
10 | Jan | 999.99 | 999.99 | 0.06177 | 999.99 | 0.056627 | 999.99 | 8 | 0 | 0.065872 | 999.99 | 999.99 | 0.78013 | 999.99 | 0.76294 | 999.99 | 16 | 0.76294 | 0.76
11 | Jan | 999.99 | 999.99 | 999.99 | 0.075314 | 0.063477 | 999.99 | 12 | 0 | 0.076531 | 999.99 | 999.99 | 999.99 | 0.74592 | 0.78172 | 999.99 | 12 | 0.74592 | 0.75
12 | Jan | 999.99 | 999.99 | 999.99 | 0.076138 | 0.060886 | 999.99 | 12 | 0 | 0.077866 | 999.99 | 999.99 | 999.99 | 0.81058 | 0.83172 | 999.99 | 12 | 0.81058 | 0.81
13 | Jan | 999.99 | 999.99 | 0.090212 | 0.069916 | 0.064478 | 0.065283 | 8 | 0 | 0.090271 | 999.99 | 999.99 | 0.81876 | 0.82176 | 0.83213 | 0.86593 | 16 | 0.81876 | 0.82
14 | Jan | 999.99 | 999.99 | 0.081379 | 0.065146 | 0.060219 | 0.060258 | 8 | 0 | 0.081615 | 999.99 | 999.99 | 0.85763 | 0.92158 | 0.9757 | 1.0227 | 8 | 0.85763 | 0.86
15 | Jan | 999.99 | 999.99 | 999.99 | 0.059414 | 0.059002 | 999.99 | 12 | 0 | 0.061927 | 999.99 | 999.99 | 999.99 | 1.0438 | 1.0605 | 999.99 | 12 | 1.0438 | 1.04
16 | Jan | 999.99 | 999.99 | 0.065107 | 999.99 | 0.056882 | 999.99 | 8 | 0 | 0.06864 | 999.99 | 999.99 | 1.0666 | 999.99 | 1.0841 | 999.99 | 8 | 1.0666 | 1.07
17 | Jan | 999.99 | 999.99 | 999.99 | 0.070249 | 0.051818 | 999.99 | 12 | 0 | 0.070838 | 999.99 | 999.99 | 999.99 | 1.0677 | 1.0935 | 999.99 | 12 | 1.0677 | 1.07
18 | Jan | 999.99 | 999.99 | 999.99 | 0.06599 | 0.050424 | 999.99 | 12 | 0 | 0.068581 | 999.99 | 999.99 | 999.99 | 1.0866 | 1.0597 | 999.99 | 16 | 1.0597 | 1.06
19 | Jan | 999.99 | 999.99 | 999.99 | 0.067423 | 0.059552 | 999.99 | 12 | 0 | 0.069935 | 999.99 | 999.99 | 999.99 | 1.0252 | 1.0179 | 999.99 | 16 | 1.0179 | 1.02
20 | Jan | 999.99 | 999.99 | 999.99 | 0.083421 | 0.066932 | 999.99 | 12 | 0 | 0.084441 | 999.99 | 999.99 | 999.99 | 1.0028 | 1.0091 | 999.99 | 12 | 1.0028 | 1
21 | Jan | 999.99 | 999.99 | 0.10857 | 999.99 | 0.076825 | 0.081222 | 8 | 0 | 0.11016 | 999.99 | 999.99 | 0.99536 | 999.99 | 0.98418 | 0.97575 | 20 | 0.97575 | 0.98
22 | Jan | 999.99 | 999.99 | 0.10246 | 0.084481 | 0.081536 | 0.081517 | 8 | 0 | 0.10315 | 999.99 | 999.99 | 0.94366 | 0.93553 | 0.92499 | 0.91381 | 20 | 0.91381 | 0.91
23 | Jan | 999.99 | 999.99 | 999.99 | 0.099085 | 0.098908 | 999.99 | 16 | 0 | 0.10166 | 999.99 | 999.99 | 999.99 | 0.86923 | 0.85886 | 999.99 | 16 | 0.85886 | 0.86
24 | Jan | 999.99 | 999.99 | 0.11752 | 0.10415 | 0.10603 | 999.99 | 8 | 0 | 0.12278 | 999.99 | 999.99 | 0.84179 | 0.84932 | 0.84096 | 999.99 | 16 | 0.84096 | 0.84
25 | Jan | 999.99 | 999.99 | 999.99 | 0.12925 | 0.11524 | 999.99 | 12 | 0 | 0.13395 | 999.99 | 999.99 | 999.99 | 0.8263 | 0.81982 | 999.99 | 16 | 0.81982 | 0.82
26 | Jan | 999.99 | 999.99 | 999.99 | 0.13587 | 0.12021 | 999.99 | 12 | 0 | 0.13667 | 999.99 | 999.99 | 999.99 | 0.81959 | 0.83437 | 999.99 | 12 | 0.81959 | 0.82
27 | Jan | 999.99 | 999.99 | 0.13832 | 999.99 | 0.12784 | 999.99 | 8 | 0 | 0.14146 | 999.99 | 999.99 | 0.82206 | 999.99 | 0.83931 | 999.99 | 8 | 0.82206 | 0.82
28 | Jan | 999.99 | 999.99 | 0.16121 | 0.13842 | 999.99 | 999.99 | 8 | 0 | 0.16121 | 999.99 | 999.99 | 0.82577 | 0.83207 | 999.99 | 999.99 | 12 | 0.82577 | 0.83
29 | Jan | 999.99 | 999.99 | 0.16125 | 999.99 | 0.15774 | 999.99 | 8 | 0 | 0.16178 | 999.99 | 999.99 | 0.81988 | 999.99 | 0.80775 | 999.99 | 16 | 0.80775 | 0.81
30 | Jan | 999.99 | 999.99 | 0.16734 | 0.15536 | 0.15432 | 999.99 | 8 | 0 | 0.17105 | 999.99 | 999.99 | 0.80133 | 0.8187 | 0.80404 | 999.99 | 8 | 0.80133 | 0.8
31 | Jan | 999.99 | 999.99 | 0.042415 | 0.024474 | 0.02312 | 999.99 | 8 | 0 | 0.043416 | 999.99 | 999.99 | 0.80934 | 0.80881 | 0.79945 | 999.99 | 16 | 0.79945 | 0.8