## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Feb_25
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | 0.02 | 0.021923 | OFF | 0.02
2 | OFF | OFF | OFF | 0.02363 | 0.019744 | OFF | 0.024592
3 | OFF | OFF | OFF | 0.02 | 0.01 | OFF | 0.02
4 | OFF | OFF | 0.01 | 0.01 | 0.01 | OFF | 0.01
5 | OFF | OFF | 0.01 | 0.01 | OFF | OFF | 0.01
6 | OFF | 0.01 | 0.01 | OFF | 0.01 | OFF | 0.01
7 | OFF | OFF | 0.01 | 0.01 | 0.020058 | OFF | 0.02
8 | OFF | OFF | OFF | 0.02 | 0.019724 | OFF | 0.02
9 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
10 | OFF | OFF | OFF | 0.01 | OFF | OFF | 0.01
11 | OFF | 0.01 | OFF | 0.024278 | 0.022727 | OFF | 0.02
12 | OFF | OFF | 0.02 | OFF | OFF | 0.022511 | 0.02
13 | 0.2 | OFF | OFF | 0.02 | OFF | 0.022492 | 0.02
14 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
15 | OFF | OFF | OFF | 0.02 | 0.022688 | OFF | 0.02
16 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
17 | OFF | OFF | 0.02 | OFF | OFF | 0.02 | 0.02
18 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
19 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
20 | OFF | OFF | 0.02 | OFF | 0.02 | 0.024219 | 0.02
21 | OFF | OFF | 0.02 | 0.02047 | OFF | OFF | 0.02
22 | OFF | 0.02 | 0.02 | OFF | 0.02 | OFF | 0.02
23 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
24 | OFF | OFF | 0.02 | 0.024926 | 0.02 | 0.02 | 0.02
25 | OFF | OFF | 0.02 | 0.02 | 0.01 | 0.02 | 0.02
26 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
27 | OFF | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02
28 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
29
30
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:03/03/25
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Feb_25 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 12:00 | 0.77 | 111 | 85.47 | 7.3 | 7.37 | 25.5919 | YES | 765
2 / 16:00 | 0.78 | 111 | 86.58 | 7.2 | 7.36 | 25.7016 | YES | 778
3 / 12:00 | 0.77 | 111 | 85.47 | 7.5 | 7.49 | 26.3572 | YES | 832
4 / 8:00 | 0.77 | 111 | 85.47 | 7.4 | 7.46 | 26.2515 | YES | 844
5 / 8:00 | 0.78 | 111 | 86.58 | 7.3 | 7.34 | 25.3486 | YES | 792
6 / 4:00 | 0.78 | 111 | 86.58 | 7.2 | 7.46 | 26.637 | YES | 811
7 / 8:00 | 0.78 | 111 | 86.58 | 7.3 | 7.33 | 25.2584 | YES | 748
8 / 12:00 | 0.79 | 111 | 87.69 | 7.1 | 7.27 | 25.0858 | YES | 780
9 / 16:00 | 0.78 | 111 | 86.58 | 7 | 7.25 | 25.0461 | YES | 761
10 / 12:00 | 0.76 | 111 | 84.36 | 7.3 | 7.39 | 25.7457 | YES | 796
11 / 4:00 | 0.75 | 111 | 83.25 | 7 | 7.4 | 26.3327 | YES | 826
12 / 20:00 | 0.75 | 111 | 83.25 | 7 | 7.35 | 25.8663 | YES | 818
13 / 12:00 | 0.76 | 111 | 84.36 | 6.9 | 7.28 | 25.4268 | YES | 840
14 / 12:00 | 0.8 | 111 | 88.8 | 6.6 | 7.27 | 25.9693 | YES | 812
15 / 12:00 | 0.82 | 111 | 91.02 | 7 | 7.34 | 25.982 | YES | 816
16 / 12:00 | 0.82 | 111 | 91.02 | 7 | 7.45 | 27.0252 | YES | 771
17 / 20:00 | 0.8 | 111 | 88.8 | 7.6 | 7.66 | 27.9224 | YES | 745
18 / 8:00 | 0.79 | 111 | 87.69 | 7.9 | 7.58 | 26.5594 | YES | 778
19 / 8:00 | 0.77 | 111 | 85.47 | 8.1 | 7.56 | 25.9588 | YES | 845
20 / 16:00 | 0.78 | 111 | 86.58 | 8.1 | 7.5 | 25.438 | YES | 802
21 / 8:00 | 0.77 | 111 | 85.47 | 8 | 7.33 | 24.0782 | YES | 806
22 / 4:00 | 0.76 | 111 | 84.36 | 8.2 | 7.27 | 23.2343 | YES | 838
23 / 12:00 | 0.75 | 111 | 83.25 | 8.1 | 7.3 | 23.6118 | YES | 761
24 / 8:00 | 0.75 | 111 | 83.25 | 8.5 | 7.42 | 23.9908 | YES | 766
25 / 8:00 | 0.77 | 111 | 85.47 | 8.4 | 7.4 | 24.035 | YES | 779
26 / 8:00 | 0.8 | 111 | 88.8 | 8.2 | 7.37 | 24.1819 | YES | 835
27 / 4:00 | 0.79 | 111 | 87.69 | 8.1 | 7.34 | 24.0583 | YES | 849
28 / 8:00 | 0.77 | 111 | 85.47 | 8.6 | 7.2 | 22.1007 | YES | 817
29 |  | 111 |  |  |  |  | NO
30 |  | 111 |  |  |  |  | NO
31 |  | 111 |  |  |  |  | NO
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Feb | 999.99 | 999.99 | 999.99 | 0.03425 | 0.021923 | 999.99 | 12 | 0 | 0.034466 | 999.99 | 999.99 | 999.99 | 0.76735 | 0.77978 | 999.99 | 12 | 0.76735 | 0.77
2 | Feb | 999.99 | 999.99 | 999.99 | 0.02363 | 0.019744 | 999.99 | 12 | 0 | 0.024592 | 999.99 | 999.99 | 999.99 | 0.78096 | 0.77937 | 999.99 | 16 | 0.77937 | 0.78
3 | Feb | 999.99 | 999.99 | 999.99 | 0.040943 | 0.021451 | 999.99 | 12 | 0 | 0.040943 | 999.99 | 999.99 | 999.99 | 0.76706 | 0.78543 | 999.99 | 12 | 0.76706 | 0.77
4 | Feb | 999.99 | 999.99 | 0.028165 | 0.019763 | 0.032856 | 999.99 | 16 | 0 | 0.032915 | 999.99 | 999.99 | 0.77118 | 0.78637 | 0.78466 | 999.99 | 8 | 0.77118 | 0.77
5 | Feb | 999.99 | 999.99 | 0.039294 | 0.021235 | 999.99 | 999.99 | 8 | 0 | 0.040335 | 999.99 | 999.99 | 0.78472 | 0.79232 | 999.99 | 999.99 | 8 | 0.78472 | 0.78
6 | Feb | 999.99 | 0.046655 | 0.021275 | 999.99 | 0.025907 | 999.99 | 4 | 0 | 0.049835 | 999.99 | 0.78125 | 0.79209 | 999.99 | 0.7879 | 999.99 | 4 | 0.78125 | 0.78
7 | Feb | 999.99 | 999.99 | 0.048088 | 0.044045 | 0.020058 | 999.99 | 8 | 0 | 0.0517 | 999.99 | 999.99 | 0.77789 | 0.78213 | 0.79438 | 999.99 | 8 | 0.77789 | 0.78
8 | Feb | 999.99 | 999.99 | 999.99 | 0.026535 | 0.019724 | 999.99 | 12 | 0 | 0.029931 | 999.99 | 999.99 | 999.99 | 0.78531 | 0.79356 | 999.99 | 12 | 0.78531 | 0.79
9 | Feb | 999.99 | 999.99 | 999.99 | 0.029283 | 0.023434 | 999.99 | 12 | 0 | 0.029303 | 999.99 | 999.99 | 999.99 | 0.77825 | 0.78555 | 999.99 | 16 | 0.77825 | 0.78
10 | Feb | 999.99 | 999.99 | 999.99 | 0.039805 | 999.99 | 999.99 | 12 | 0 | 0.061829 | 999.99 | 999.99 | 999.99 | 0.76394 | 999.99 | 999.99 | 12 | 0.76394 | 0.76
11 | Feb | 999.99 | 0.042572 | 999.99 | 0.024278 | 0.022727 | 999.99 | 4 | 0 | 0.04428 | 999.99 | 0.75416 | 999.99 | 0.75499 | 0.76924 | 999.99 | 4 | 0.75416 | 0.75
12 | Feb | 999.99 | 999.99 | 0.02681 | 999.99 | 999.99 | 0.022511 | 8 | 0 | 0.030736 | 999.99 | 999.99 | 0.75775 | 999.99 | 999.99 | 0.75104 | 20 | 0.75104 | 0.75
13 | Feb | 0.027615 | 999.99 | 999.99 | 0.034132 | 999.99 | 0.022492 | 12 | 0 | 0.035683 | 0.75675 | 999.99 | 999.99 | 0.76488 | 999.99 | 0.78943 | 12 | 0.76488 | 0.76
14 | Feb | 999.99 | 999.99 | 999.99 | 0.029755 | 0.024651 | 999.99 | 12 | 0 | 0.029755 | 999.99 | 999.99 | 999.99 | 0.79927 | 0.83943 | 999.99 | 12 | 0.79927 | 0.8
15 | Feb | 999.99 | 999.99 | 999.99 | 0.037744 | 0.022688 | 999.99 | 12 | 0 | 0.037842 | 999.99 | 999.99 | 999.99 | 0.81982 | 0.84043 | 999.99 | 12 | 0.81982 | 0.82
16 | Feb | 999.99 | 999.99 | 999.99 | 0.028263 | 0.029323 | 999.99 | 16 | 0 | 0.029323 | 999.99 | 999.99 | 999.99 | 0.82394 | 0.83207 | 999.99 | 12 | 0.82394 | 0.82
17 | Feb | 999.99 | 999.99 | 0.043868 | 999.99 | 999.99 | 0.038647 | 8 | 0 | 0.044437 | 999.99 | 999.99 | 0.79962 | 999.99 | 999.99 | 0.80174 | 20 | 0.79962 | 0.8
18 | Feb | 0.037037 | 999.99 | 0.030932 | 0.028145 | 0.027438 | 999.99 | 0 | 0 | 0.037253 | 0.80292 | 999.99 | 0.79085 | 0.80639 | 0.80486 | 999.99 | 8 | 0.79085 | 0.79
19 | Feb | 999.99 | 999.99 | 0.046498 | 0.039314 | 0.024926 | 999.99 | 8 | 0 | 0.046498 | 999.99 | 999.99 | 0.78955 | 0.79868 | 0.79285 | 999.99 | 8 | 0.78955 | 0.79
20 | Feb | 999.99 | 999.99 | 0.045517 | 999.99 | 0.029421 | 0.024219 | 8 | 0 | 0.048756 | 999.99 | 999.99 | 0.78425 | 999.99 | 0.78237 | 0.78684 | 16 | 0.78237 | 0.78
21 | Feb | 999.99 | 999.99 | 0.046989 | 0.02047 | 999.99 | 999.99 | 8 | 0 | 0.049678 | 999.99 | 999.99 | 0.77371 | 0.78991 | 999.99 | 999.99 | 8 | 0.77371 | 0.77
22 | Feb | 999.99 | 0.045634 | 0.027379 | 999.99 | 0.026418 | 999.99 | 4 | 0 | 0.04852 | 999.99 | 0.75893 | 0.77059 | 999.99 | 0.77006 | 999.99 | 4 | 0.75893 | 0.76
23 | Feb | 999.99 | 999.99 | 0.03476 | 0.031835 | 0.025358 | 0.024729 | 8 | 0 | 0.038548 | 999.99 | 999.99 | 0.75875 | 0.75045 | 0.75793 | 0.76223 | 12 | 0.75045 | 0.75
24 | Feb | 999.99 | 999.99 | 0.032463 | 0.024926 | 0.02577 | 0.031286 | 20 | 0 | 0.033249 | 999.99 | 999.99 | 0.75022 | 0.77171 | 0.78979 | 0.78255 | 8 | 0.75022 | 0.75
25 | Feb | 999.99 | 999.99 | 999.99 | 0.029264 | 0.028263 | 0.028302 | 16 | 0 | 0.031796 | 999.99 | 999.99 | 999.99 | 0.78007 | 0.78832 | 0.7998 | 8 | 0.77 | 0.77
26 | Feb | 999.99 | 999.99 | 0.037783 | 0.025534 | 999.99 | 999.99 | 8 | 0 | 0.041787 | 999.99 | 999.99 | 0.79939 | 0.81434 | 999.99 | 999.99 | 8 | 0.79939 | 0.8
27 | Feb | 999.99 | 0.048343 | 999.99 | 0.028341 | 0.025907 | 999.99 | 4 | 0 | 0.048697 | 999.99 | 0.78284 | 999.99 | 0.78873 | 0.80133 | 999.99 | 4 | 0.78284 | 0.78
28 | Feb | 999.99 | 999.99 | 0.066186 | 0.027851 | 999.99 | 999.99 | 8 | 0 | 0.069307 | 999.99 | 999.99 | 0.76788 | 0.77518 | 999.99 | 999.99 | 8 | 0.76788 | 0.77