## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Mar_25
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
2 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
3 | OFF | OFF | 0.01 | 0.02 | OFF | OFF | 0.02
4 | OFF | OFF | 0.01 | OFF | 0.01 | 0.022551 | 0.02
5 | OFF | OFF | 0.01 | OFF | 0.02 | 0.023061 | 0.02
6 | OFF | OFF | 0.02 | 0.020902 | 0.019606 | OFF | 0.02
7 | OFF | OFF | 0.01 | 0.02 | 0.019547 | OFF | 0.02
8 | OFF | OFF | OFF | 0.02 | 0.01994 | OFF | 0.02
9 | OFF | OFF | OFF | 0.02 | 0.020725 | OFF | 0.02
10 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
11 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
12 | OFF | 0.02 | 0.023473 | OFF | OFF | 0.02 | 0.02
13 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
14 | OFF | OFF | 0.02 | 0.02 | 0.022511 | OFF | 0.02
15 | OFF | OFF | 0.02 | 0.024219 | 0.02 | OFF | 0.02
16 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
17 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
18 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
19 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
20 | OFF | OFF | 0.02 | OFF | OFF | 0.02 | 0.02
21 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
22 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
23 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
24 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
25 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
26 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
27 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
28 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
29 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
30 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
31 | OFF | OFF | 0.02 | OFF | OFF | 0.02 | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J. Dues
[5 empty] | SIGNATURE:Zachary J. Dues |  |  | DATE:04/01/2025
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Mar_25 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 4:00 | 0.76 | 111 | 84.36 | 8.4 | 7.14 | 21.9021 | YES | 840
2 / 8:00 | 0.75 | 111 | 83.25 | 8.3 | 7.1 | 21.7149 | YES | 784
3 / 8:00 | 0.77 | 111 | 85.47 | 8.3 | 7.28 | 23.1888 | YES | 756
4 / 8:00 | 0.77 | 111 | 85.47 | 8.4 | 7.16 | 22.0816 | YES | 734
5 / 16:00 | 0.76 | 111 | 84.36 | 8.3 | 7.12 | 21.8926 | YES | 740
6 / 8:00 | 0.76 | 111 | 84.36 | 8.4 | 7.15 | 21.9792 | YES | 819
7 / 8:00 | 0.77 | 111 | 85.47 | 8.4 | 7.13 | 21.85 | YES | 843
8 / 12:00 | 0.76 | 111 | 84.36 | 8.1 | 7.1 | 22.0279 | YES | 811
9 / 12:00 | 0.75 | 111 | 83.25 | 8.1 | 7.12 | 22.1584 | YES | 869
10 / 8:00 | 0.74 | 111 | 82.14 | 8.2 | 7.28 | 23.2637 | YES | 788
11 / 8:00 | 0.79 | 111 | 87.69 | 8.2 | 7.33 | 23.8141 | YES | 756
12 / 4:00 | 0.78 | 111 | 86.58 | 8.2 | 7.05 | 21.551 | YES | 798
13 / 12:00 | 0.78 | 111 | 86.58 | 8.2 | 7.03 | 21.4004 | YES | 812
14 / 8:00 | 0.78 | 111 | 86.58 | 8.2 | 7.03 | 21.4004 | YES | 809
15 / 8:00 | 0.79 | 111 | 87.69 | 8.2 | 7.01 | 21.2749 | YES | 824
16 / 8:00 | 0.78 | 111 | 86.58 | 8.2 | 7.01 | 21.2509 | YES | 797
17 / 8:00 | 0.78 | 111 | 86.58 | 8.3 | 7.2 | 22.5687 | YES | 832
18 / 8:00 | 0.77 | 111 | 85.47 | 8.5 | 7.32 | 23.209 | YES | 752
19 / 8:00 | 0.77 | 111 | 85.47 | 8.7 | 7.36 | 23.2292 | YES | 763
20 / 8:00 | 0.77 | 111 | 85.47 | 8.8 | 7.4 | 23.4043 | YES | 804
21 / 8:00 | 0.76 | 111 | 84.36 | 8.8 | 7.25 | 22.1728 | YES | 846
22 / 8:00 | 0.75 | 111 | 83.25 | 8.9 | 7.24 | 21.9249 | YES | 772
23 / 12:00 | 0.79 | 111 | 87.69 | 9.1 | 7.24 | 21.7356 | YES | 811
24 / 16:00 | 0.78 | 111 | 86.58 | 9.3 | 7.42 | 22.8276 | YES | 7.93
25 / 8:00 | 0.78 | 111 | 86.58 | 9.7 | 7.4 | 22.0758 | YES | 808
26 / 8:00 | 0.77 | 111 | 85.47 | 10 | 7.26 | 20.5855 | YES | 764
27 / 12:00 | 0.78 | 111 | 86.58 | 10 | 7.34 | 21.193 | YES | 778
28 / 8:00 | 0.75 | 111 | 83.25 | 9.9 | 7.21 | 20.3169 | YES | 793
29 / 8:00 | 0.73 | 111 | 81.03 | 9.9 | 7.19 | 20.1308 | YES | 803
30 / 12:00 | 0.75 | 111 | 83.25 | 9.9 | 7.21 | 20.3169 | YES | 807
31 / 8:00 | 0.76 | 111 | 84.36 | 9.8 | 7.31 | 21.2013 | YES | 795
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Mar | 999.99 | 0.046537 | 0.043966 | 0.042199 | 0.031639 | 999.99 | 4 | 0 | 0.049128 | 999.99 | 0.75605 | 0.76441 | 0.75817 | 0.77289 | 999.99 | 4 | 0.75605 | 0.76
2 | Mar | 999.99 | 999.99 | 0.046086 | 0.037037 | 0.026496 | 999.99 | 8 | 0 | 0.046086 | 999.99 | 999.99 | 0.74533 | 0.76682 | 0.78961 | 999.99 | 8 | 0.74533 | 0.75
3 | Mar | 999.99 | 999.99 | 0.044025 | 0.019901 | 999.99 | 999.99 | 8 | 0 | 0.04481 | 999.99 | 999.99 | 0.77471 | 0.79685 | 999.99 | 999.99 | 8 | 0.77471 | 0.77
4 | Mar | 999.99 | 999.99 | 0.037155 | 999.99 | 0.020509 | 0.022551 | 8 | 0 | 0.038764 | 999.99 | 999.99 | 0.76594 | 999.99 | 0.78997 | 0.79273 | 8 | 0.76594 | 0.77
5 | Mar | 999.99 | 999.99 | 0.049403 | 999.99 | 0.030854 | 0.023061 | 8 | 0 | 0.050915 | 999.99 | 999.99 | 0.76582 | 999.99 | 0.76264 | 0.77937 | 16 | 0.76264 | 0.76
6 | Mar | 999.99 | 999.99 | 0.040138 | 0.020902 | 0.019606 | 999.99 | 8 | 0 | 0.044359 | 999.99 | 999.99 | 0.76388 | 0.78502 | 0.78955 | 999.99 | 8 | 0.76388 | 0.76
7 | Mar | 999.99 | 999.99 | 0.039549 | 0.026143 | 0.019547 | 999.99 | 8 | 0 | 0.043632 | 999.99 | 999.99 | 0.76729 | 0.77595 | 0.78561 | 999.99 | 8 | 0.76729 | 0.77
8 | Mar | 999.99 | 999.99 | 999.99 | 0.028891 | 0.01994 | 999.99 | 12 | 0 | 0.032463 | 999.99 | 999.99 | 999.99 | 0.76352 | 0.77754 | 999.99 | 12 | 0.76352 | 0.76
9 | Mar | 999.99 | 999.99 | 999.99 | 0.030069 | 0.020725 | 999.99 | 12 | 0 | 0.034485 | 999.99 | 999.99 | 999.99 | 0.75964 | 0.75905 | 999.99 | 12 | 0.75 | 0.75
10 | Mar | 999.99 | 999.99 | 0.045301 | 0.021373 | 0.018978 | 999.99 | 8 | 0 | 0.048618 | 999.99 | 999.99 | 0.74397 | 0.78125 | 0.79314 | 999.99 | 8 | 0.74397 | 0.74
11 | Mar | 999.99 | 999.99 | 0.036585 | 0.027124 | 999.99 | 999.99 | 8 | 0 | 0.039059 | 999.99 | 999.99 | 0.77907 | 0.7965 | 999.99 | 999.99 | 8 | 0.77907 | 0.78
12 | Mar | 999.99 | 0.025829 | 0.023473 | 999.99 | 999.99 | 0.029126 | 20 | 0 | 0.030167 | 999.99 | 0.77854 | 0.80127 | 999.99 | 999.99 | 0.79226 | 4 | 0.77854 | 0.78
13 | Mar | 999.99 | 999.99 | 999.99 | 0.027811 | 0.025142 | 999.99 | 12 | 0 | 0.031776 | 999.99 | 999.99 | 999.99 | 0.7799 | 0.78826 | 999.99 | 12 | 0.7799 | 0.78
14 | Mar | 999.99 | 999.99 | 0.049089 | 0.027811 | 0.022511 | 999.99 | 8 | 0 | 0.05115 | 999.99 | 999.99 | 0.77742 | 0.78873 | 0.79291 | 999.99 | 8 | 0.77742 | 0.78
15 | Mar | 999.99 | 999.99 | 0.034328 | 0.024219 | 0.026594 | 999.99 | 8 | 0 | 0.038372 | 999.99 | 999.99 | 0.78843 | 0.80127 | 0.80404 | 999.99 | 8 | 0.78843 | 0.79
16 | Mar | 999.99 | 999.99 | 0.059022 | 0.031717 | 0.02418 | 999.99 | 8 | 0 | 0.059022 | 999.99 | 999.99 | 0.78431 | 0.78637 | 0.81458 | 999.99 | 8 | 0.78431 | 0.78
17 | Mar | 999.99 | 999.99 | 0.045733 | 0.026653 | 999.99 | 999.99 | 8 | 0 | 0.049835 | 999.99 | 999.99 | 0.78402 | 0.79903 | 999.99 | 999.99 | 8 | 0.78402 | 0.78
18 | Mar | 999.99 | 999.99 | 0.053506 | 0.031109 | 0.02522 | 999.99 | 8 | 0 | 0.053545 | 999.99 | 999.99 | 0.77554 | 0.78478 | 0.80062 | 999.99 | 8 | 0.77554 | 0.78
19 | Mar | 999.99 | 999.99 | 0.029323 | 0.028852 | 0.030088 | 999.99 | 8 | 0 | 0.030756 | 999.99 | 999.99 | 0.77407 | 0.78643 | 0.79203 | 999.99 | 8 | 0.77407 | 0.77
20 | Mar | 999.99 | 999.99 | 0.045497 | 999.99 | 999.99 | 0.053133 | 20 | 0 | 0.054095 | 999.99 | 999.99 | 0.77289 | 999.99 | 999.99 | 0.77901 | 8 | 0.77289 | 0.77
21 | Mar | 999.99 | 999.99 | 0.052367 | 0.03425 | 0.037488 | 999.99 | 8 | 0 | 0.052564 | 999.99 | 999.99 | 0.75923 | 0.77165 | 0.78166 | 999.99 | 8 | 0.75923 | 0.76
22 | Mar | 999.99 | 999.99 | 0.20316 | 0.038313 | 0.030147 | 0.030952 | 8 | 0 | 0.20316 | 999.99 | 999.99 | 0.74586 | 0.768 | 0.79108 | 0.80027 | 8 | 0.74586 | 0.75
23 | Mar | 999.99 | 999.99 | 999.99 | 0.036782 | 0.034171 | 999.99 | 12 | 0 | 0.040079 | 999.99 | 999.99 | 999.99 | 0.78961 | 0.80422 | 999.99 | 12 | 0.78961 | 0.79
24 | Mar | 999.99 | 999.99 | 0.051504 | 999.99 | 0.04536 | 999.99 | 8 | 0 | 0.052819 | 999.99 | 999.99 | 0.77854 | 999.99 | 0.77972 | 999.99 | 16 | 0.77854 | 0.78
25 | Mar | 999.99 | 999.99 | 0.045399 | 0.041198 | 0.04587 | 999.99 | 8 | 0 | 0.04801 | 999.99 | 999.99 | 0.77677 | 0.79632 | 0.80327 | 999.99 | 8 | 0.77677 | 0.78
26 | Mar | 999.99 | 999.99 | 0.059924 | 0.051111 | 0.04534 | 999.99 | 8 | 0 | 0.063301 | 999.99 | 999.99 | 0.76965 | 0.78331 | 0.79126 | 999.99 | 8 | 0.76965 | 0.77
27 | Mar | 999.99 | 999.99 | 0.05541 | 0.066873 | 999.99 | 999.99 | 12 | 0 | 0.075628 | 999.99 | 999.99 | 0.78031 | 0.77919 | 999.99 | 999.99 | 12 | 0.77919 | 0.78
28 | Mar | 999.99 | 999.99 | 0.093333 | 999.99 | 0.058295 | 999.99 | 8 | 0 | 0.095905 | 999.99 | 999.99 | 0.75192 | 999.99 | 0.76594 | 999.99 | 8 | 0.75192 | 0.75
29 | Mar | 999.99 | 999.99 | 0.10568 | 0.065087 | 0.060984 | 999.99 | 8 | 0 | 0.10568 | 999.99 | 999.99 | 0.72931 | 0.74138 | 0.75911 | 999.99 | 8 | 0.72931 | 0.73
30 | Mar | 999.99 | 999.99 | 0.10138 | 0.066677 | 0.062182 | 999.99 | 8 | 0 | 0.10433 | 999.99 | 999.99 | 0.74521 | 0.76082 | 0.76788 | 999.99 | 12 | 0.74521 | 0.75
31 | Mar | 999.99 | 999.99 | 0.0792 | 999.99 | 999.99 | 0.079828 | 20 | 0 | 0.0803 | 999.99 | 999.99 | 0.75398 | 999.99 | 999.99 | 0.76423 | 8 | 0.75398 | 0.75