## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | May_25
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
2 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
3 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
4 | OFF | OFF | 0.02 | 0.023414 | 0.024474 | OFF | 0.02
5 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
6 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
7 | OFF | 0.02 | 0.02 | 0.02 | OFF | OFF | 0.02
8 | OFF | 0.01 | OFF | OFF | 0.01 | OFF | 0.01
9 | OFF | OFF | 0.01 | OFF | 0.01 | OFF | 0.01
10 | OFF | OFF | OFF | 0.01 | 0.01 | OFF | 0.01
11 | OFF | OFF | OFF | 0.01 | 0.01 | OFF | 0.01
12 | OFF | OFF | 0.01 | 0.01 | 0.02 | OFF | 0.02
13 | OFF | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02
14 | OFF | OFF | 0.02 | OFF | OFF | OFF | 0.02
15 | 0.02 | OFF | OFF | 0.02 | OFF | OFF | 0.02
16 | 0.02 | 0.02 | OFF | 0.02 | OFF | OFF | 0.02
17 | OFF | 0.02 | OFF | 0.02 | OFF | OFF | 0.02
18 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
19 | 0.02 | OFF | OFF | OFF | 0.02 | OFF | 0.02
20 | OFF | OFF | 0.02 | OFF | OFF | OFF | 0.02
21 | 0.02 | OFF | 0.02 | OFF | OFF | OFF | 0.02
22 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
23 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
24 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
25 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
26 | 0.02 | 0.02 | OFF | OFF | OFF | OFF | 0.02
27 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
28 | OFF | 0.02 | OFF | OFF | 0.02 | 0.02 | 0.02
29 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
30 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
31 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:06/02/2025
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | May_25 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 12:00 | 0.75 | 111 | 83.25 | 11.3 | 7.24 | 18.7419 | YES | 810
2 / 8:00 | 0.81 | 111 | 89.91 | 11.9 | 7.19 | 17.8405 | YES | 810
3 / 8:00 | 0.81 | 111 | 89.91 | 11.5 | 7.16 | 18.1185 | YES | 811
4 / 8:00 | 0.82 | 111 | 91.02 | 11.4 | 7.18 | 18.3819 | YES | 763
5 / 20:00 | 0.8 | 111 | 88.8 | 11.5 | 7.24 | 18.6036 | YES | 849
6 / 8:00 | 0.77 | 111 | 85.47 | 11.8 | 7.15 | 17.6334 | YES | 818
7 / 4:00 | 0.77 | 111 | 85.47 | 12.4 | 7.24 | 17.4976 | YES | 898
8 / 4:00 | 0.8 | 111 | 88.8 | 12.6 | 7.45 | 18.4553 | YES | 855
9 / 8:00 | 0.79 | 111 | 87.69 | 13 | 7.48 | 18.1507 | YES | 892
10 / 12:00 | 0.79 | 111 | 87.69 | 13.4 | 7.57 | 18.2716 | YES | 868
11 / 12:00 | 0.8 | 111 | 88.8 | 13.5 | 7.58 | 18.2383 | YES | 873
12 / 8:00 | 0.81 | 111 | 89.91 | 13.7 | 7.62 | 18.2859 | YES | 833
13 / 8:00 | 0.79 | 111 | 87.69 | 13.5 | 7.57 | 18.1505 | YES | 840
14 / 8:00 | 0.79 | 111 | 87.69 | 13.4 | 7.5 | 17.8054 | YES | 858
15 / 12:00 | 0.77 | 111 | 85.47 | 13.5 | 7.6 | 18.311 | YES | 812
16 / 12:00 | 0.77 | 111 | 85.47 | 13.3 | 7.5 | 17.8836 | YES | 811
17 / 4:00 | 0.77 | 111 | 85.47 | 13.3 | 7.44 | 17.4916 | YES | 870
18 / 8:00 | 0.76 | 111 | 84.36 | 13.3 | 7.4 | 17.2154 | YES | 867
19 / 0:00 | 0.77 | 111 | 85.47 | 13.4 | 7.47 | 17.5693 | YES | 857
20 / 8:00 | 0.79 | 111 | 87.69 | 13.4 | 7.46 | 17.5443 | YES | 881
21 / 8:00 | 0.78 | 111 | 86.58 | 13.2 | 7.46 | 17.759 | YES | 800
22 / 0:00 | 0.78 | 111 | 86.58 | 13.5 | 7.5 | 17.6674 | YES | 839
23 / 16:00 | 0.75 | 111 | 83.25 | 13.4 | 7.48 | 17.5943 | YES | 810
24 / 12:00 | 0.72 | 111 | 79.92 | 13.6 | 7.36 | 16.5519 | YES | 833
25 / 8:00 | 0.74 | 111 | 82.14 | 13.8 | 7.39 | 16.5527 | YES | 846
26 / 0:00 | 0.76 | 111 | 84.36 | 13.8 | 7.44 | 16.9 | YES | 831
27 / 8:00 | 0.79 | 111 | 87.69 | 14 | 7.43 | 16.6717 | YES | 856
28 / 4:00 | 0.78 | 111 | 86.58 | 14.5 | 7.35 | 15.637 | YES | 880
29 / 12:00 | 0.78 | 111 | 86.58 | 14.8 | 7.42 | 15.7299 | YES | 886
30 / 8:00 | 0.77 | 111 | 85.47 | 14.8 | 7.36 | 15.3666 | YES | 877
31 / 8:00 | 0.75 | 111 | 83.25 | 15.3 | 7.3 | 14.5018 | YES | 879
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | May | 999.99 | 999.99 | 999.99 | 0.035211 | 0.0263 | 999.99 | 12 | 0 | 0.036801 | 999.99 | 999.99 | 999.99 | 0.74974 | 0.82218 | 999.99 | 12 | 0.74974 | 0.75
2 | May | 999.99 | 999.99 | 0.032876 | 0.048284 | 0.027615 | 0.034387 | 12 | 0 | 0.049128 | 999.99 | 999.99 | 0.80757 | 0.81376 | 0.82253 | 0.83301 | 8 | 0.80757 | 0.81
3 | May | 999.99 | 999.99 | 0.061868 | 0.028204 | 0.025809 | 999.99 | 8 | 0 | 0.066324 | 999.99 | 999.99 | 0.8124 | 0.81976 | 0.83525 | 999.99 | 8 | 0.8124 | 0.81
4 | May | 999.99 | 999.99 | 0.035761 | 0.023414 | 0.024474 | 999.99 | 8 | 0 | 0.039549 | 999.99 | 999.99 | 0.81646 | 0.83048 | 0.82412 | 999.99 | 8 | 0.81646 | 0.82
5 | May | 999.99 | 999.99 | 0.039608 | 0.034446 | 0.028027 | 0.028538 | 8 | 0 | 0.039608 | 999.99 | 999.99 | 0.80445 | 0.80504 | 0.81058 | 0.80151 | 20 | 0.80151 | 0.8
6 | May | 999.99 | 999.99 | 0.030186 | 0.024592 | 0.028223 | 999.99 | 8 | 0 | 0.032974 | 999.99 | 999.99 | 0.7733 | 0.78525 | 0.78843 | 999.99 | 8 | 0.7733 | 0.77
7 | May | 999.99 | 0.035977 | 0.027536 | 0.024415 | 999.99 | 999.99 | 8 | 0 | 0.048971 | 999.99 | 0.7703 | 0.78702 | 0.81658 | 999.99 | 999.99 | 4 | 0.7703 | 0.77
8 | May | 999.99 | 0.22387 | 999.99 | 999.99 | 0.035957 | 999.99 | 4 | 0 | 0.22406 | 999.99 | 0.7965 | 999.99 | 999.99 | 0.81358 | 999.99 | 4 | 0.7965 | 0.8
9 | May | 999.99 | 999.99 | 0.0443 | 999.99 | 0.034662 | 999.99 | 8 | 0 | 0.045929 | 999.99 | 999.99 | 0.79497 | 999.99 | 0.81882 | 999.99 | 8 | 0.79497 | 0.79
10 | May | 999.99 | 999.99 | 999.99 | 0.042788 | 0.039608 | 999.99 | 12 | 0 | 0.04638 | 999.99 | 999.99 | 999.99 | 0.78726 | 0.81882 | 999.99 | 12 | 0.78726 | 0.79
11 | May | 999.99 | 999.99 | 999.99 | 0.045006 | 0.036173 | 999.99 | 12 | 0 | 0.048932 | 999.99 | 999.99 | 999.99 | 0.81364 | 0.82459 | 999.99 | 12 | 0.81364 | 0.81
12 | May | 999.99 | 999.99 | 0.061672 | 0.039471 | 0.035133 | 999.99 | 8 | 0 | 0.065008 | 999.99 | 999.99 | 0.81352 | 0.81699 | 0.81788 | 999.99 | 8 | 0.81352 | 0.81
13 | May | 999.99 | 999.99 | 0.042828 | 999.99 | 0.037861 | 0.04373 | 20 | 0 | 0.046753 | 999.99 | 999.99 | 0.78431 | 999.99 | 0.80003 | 0.81393 | 8 | 0.78431 | 0.78
14 | May | 999.99 | 999.99 | 0.071408 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.074391 | 999.99 | 999.99 | 0.78973 | 999.99 | 999.99 | 999.99 | 8 | 0.78973 | 0.79
15 | May | 0.045222 | 999.99 | 999.99 | 0.041022 | 999.99 | 999.99 | 0 | 0 | 0.048775 | 0.78007 | 999.99 | 999.99 | 0.79049 | 999.99 | 999.99 | 12 | 0.79049 | 0.79
16 | May | 0.07659 | 0.04905 | 999.99 | 0.042415 | 999.99 | 999.99 | 4 | 0 | 0.050463 | 0.76959 | 0.7786 | 999.99 | 0.78773 | 999.99 | 999.99 | 4 | 0.7786 | 0.78
17 | May | 999.99 | 0.058904 | 999.99 | 0.043259 | 999.99 | 999.99 | 4 | 0 | 0.06071 | 999.99 | 0.76729 | 999.99 | 0.78543 | 999.99 | 999.99 | 4 | 0.76729 | 0.77
18 | May | 999.99 | 999.99 | 0.074568 | 0.048304 | 999.99 | 999.99 | 8 | 0 | 0.074587 | 999.99 | 999.99 | 0.76246 | 0.77536 | 999.99 | 999.99 | 8 | 0.76246 | 0.76
19 | May | 0.085011 | 999.99 | 999.99 | 999.99 | 0.057844 | 999.99 | 16 | 0 | 0.065028 | 0.7657 | 999.99 | 999.99 | 999.99 | 0.78867 | 999.99 | 0 | 0.77 | 0.77
20 | May | 999.99 | 999.99 | 0.09084 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.094001 | 999.99 | 999.99 | 0.78902 | 999.99 | 999.99 | 999.99 | 8 | 0.78902 | 0.79
21 | May | 0.061279 | 999.99 | 0.065597 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.068404 | 0.79032 | 999.99 | 0.78366 | 999.99 | 999.99 | 999.99 | 8 | 0.78366 | 0.78
22 | May | 0.099183 | 999.99 | 0.061672 | 0.058452 | 999.99 | 999.99 | 8 | 0 | 0.064223 | 0.78172 | 999.99 | 0.81069 | 0.80151 | 999.99 | 999.99 | 0 | 0.78 | 0.78
23 | May | 999.99 | 999.99 | 0.066952 | 0.066324 | 0.065951 | 999.99 | 8 | 0 | 0.069013 | 999.99 | 999.99 | 0.75593 | 0.75475 | 0.75393 | 999.99 | 16 | 0.75393 | 0.75
24 | May | 999.99 | 999.99 | 999.99 | 0.075667 | 0.067953 | 999.99 | 12 | 0 | 0.076707 | 999.99 | 999.99 | 999.99 | 0.72083 | 0.75522 | 999.99 | 12 | 0.72083 | 0.72
25 | May | 999.99 | 999.99 | 0.083381 | 0.069189 | 999.99 | 999.99 | 8 | 0 | 0.083381 | 999.99 | 999.99 | 0.7352 | 0.78508 | 999.99 | 999.99 | 8 | 0.7352 | 0.74
26 | May | 0.10878 | 0.081242 | 999.99 | 999.99 | 999.99 | 999.99 | 4 | 0 | 0.08136 | 0.76276 | 0.78814 | 999.99 | 999.99 | 999.99 | 999.99 | 0 | 0.763 | 0.76
27 | May | 0.085482 | 999.99 | 0.081418 | 0.085717 | 999.99 | 999.99 | 12 | 0 | 0.086856 | 0.79362 | 999.99 | 0.79385 | 0.80887 | 999.99 | 999.99 | 8 | 0.79385 | 0.79
28 | May | 999.99 | 0.098535 | 999.99 | 999.99 | 0.13679 | 0.091645 | 16 | 0 | 0.13921 | 999.99 | 0.77306 | 999.99 | 999.99 | 0.78496 | 0.80251 | 4 | 0.77306 | 0.77
29 | May | 999.99 | 999.99 | 999.99 | 0.11159 | 0.097809 | 999.99 | 12 | 0 | 0.11159 | 999.99 | 999.99 | 999.99 | 0.77889 | 0.80628 | 999.99 | 12 | 0.77889 | 0.78
30 | May | 999.99 | 999.99 | 0.11334 | 999.99 | 0.11373 | 999.99 | 16 | 0 | 0.11504 | 999.99 | 999.99 | 0.76635 | 999.99 | 0.78926 | 999.99 | 8 | 0.76635 | 0.77
31 | May | 999.99 | 999.99 | 0.12649 | 0.10921 | 0.10982 | 999.99 | 8 | 0 | 0.128 | 999.99 | 999.99 | 0.75004 | 0.78154 | 0.80763 | 999.99 | 8 | 0.75004 | 0.75