## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Jun_25
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
2 | OFF | OFF | 0.02 | OFF | OFF | OFF | 0.02
3 | 0.02 | OFF | 0.02 | OFF | OFF | 0.02 | 0.02
4 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
5 | OFF | OFF | 0.02 | 0.03 | OFF | OFF | 0.03
6 | 0.01 | OFF | 0.01 | OFF | 0.01 | OFF | 0.01
7 | OFF | OFF | 0.01 | 0.01 | 0.01 | OFF | 0.01
8 | OFF | OFF | 0.01 | OFF | 0.01 | OFF | 0.01
9 | OFF | OFF | 0.01 | 0.02 | 0.02 | OFF | 0.02
10 | OFF | OFF | 0.02 | OFF | OFF | 0.02 | 0.02
11 | 0.02 | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02
12 | OFF | OFF | 0.02 | 0.02 | 0.022688 | OFF | 0.02
13 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
14 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
15 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
16 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
17 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
18 | OFF | OFF | OFF | OFF | 0.02 | OFF | 0.02
19 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
20 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
21 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
22 | OFF | OFF | 0.02 | OFF | 0.02 | OFF | 0.02
23 | OFF | OFF | 0.02 | OFF | OFF | OFF | 0.02
24 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
25 | OFF | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02
26 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
27 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
28 | OFF | OFF | 0.2 | OFF | 0.02 | OFF | 0.02
29 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
30 | OFF | OFF | 0.02 | OFF | OFF | OFF | 0.02
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:07/01/2025
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Jun_25 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 12:00 | 0.78 | 111 | 86.58 | 15.3 | 7.31 | 14.6056 | YES | 848
2 / 8:00 | 0.77 | 111 | 85.47 | 15.7 | 7.42 | 14.796 | YES | 848
3 / 20:00 | 0.78 | 111 | 86.58 | 15.9 | 7.5 | 15.0565 | YES | 858
4 / 8:00 | 0.79 | 111 | 87.69 | 16.2 | 7.41 | 14.2894 | YES | 826
5 / 8:00 | 0.76 | 111 | 84.36 | 16.2 | 7.52 | 14.8339 | YES | 839
6 / 16:00 | 0.75 | 111 | 83.25 | 16.5 | 7.42 | 13.9936 | YES | 865
7 / 8:00 | 0.72 | 111 | 79.92 | 16.7 | 7.4 | 13.6584 | YES | 872
8 / 8:00 | 0.75 | 111 | 83.25 | 17.2 | 7.41 | 13.3034 | YES | 874
9 / 8:00 | 0.76 | 111 | 84.36 | 17.5 | 7.48 | 13.3981 | YES | 824
10 / 20:00 | 0.75 | 111 | 83.25 | 18.1 | 7.43 | 12.618 | YES | 822
11 / 16:00 | 0.74 | 111 | 82.14 | 18.6 | 7.45 | 12.2787 | YES | 859
12 / 8:00 | 0.73 | 111 | 81.03 | 18.5 | 7.37 | 11.9842 | YES | 829
13 / 8:00 | 0.75 | 111 | 83.25 | 18.5 | 7.32 | 11.7896 | YES | 882
14 / 8:00 | 0.77 | 111 | 85.47 | 18.3 | 7.34 | 12.0664 | YES | 889
15 / 16:00 | 0.75 | 111 | 83.25 | 18.1 | 7.3 | 12.0208 | YES | 889
16 / 8:00 | 0.78 | 111 | 86.58 | 17.9 | 7.48 | 13.0736 | YES | 873
17 / 8:00 | 0.81 | 111 | 89.91 | 17.6 | 7.44 | 13.1872 | YES | 913
18 / 16:00 | 0.81 | 111 | 89.91 | 17.7 | 7.4 | 12.9055 | YES | 862
19 / 12:00 | 0.8 | 111 | 88.8 | 17.6 | 7.37 | 12.8333 | YES | 851
20 / 8:00 | 0.78 | 111 | 86.58 | 17.7 | 7.31 | 12.437 | YES | 851
21 / 12:00 | 0.77 | 111 | 85.47 | 17.5 | 7.38 | 12.9233 | YES | 863
22 / 8:00 | 0.78 | 111 | 86.58 | 17.2 | 7.32 | 12.9093 | YES | 862
23 / 8:00 | 0.75 | 111 | 83.25 | 17.1 | 7.47 | 13.695 | YES | 902
24 / 0:00 | 0.77 | 111 | 85.47 | 17 | 7.45 | 13.7162 | YES | 868
25 / 16:00 | 0.74 | 111 | 82.14 | 16.7 | 7.35 | 13.4375 | YES | 867
26 / 8:00 | 0.68 | 111 | 75.48 | 16.8 | 7.43 | 13.6568 | YES | 871
27 / 8:00 | 0.74 | 111 | 82.14 | 16.6 | 7.29 | 13.2291 | YES | 817
28 / 8:00 | 0.75 | 111 | 83.25 | 16.8 | 7.32 | 13.2147 | YES | 854
29 / 12:00 | 0.79 | 111 | 87.69 | 17.3 | 7.3 | 12.7425 | YES | 845
30 / 8:00 | 0.81 | 111 | 89.91 | 17.6 | 7.47 | 13.3352 | YES | 828
31 |  | 111 |  |  |  |  | NO
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Jun | 999.99 | 999.99 | 999.99 | 0.12142 | 0.11267 | 999.99 | 12 | 0 | 0.12392 | 999.99 | 999.99 | 999.99 | 0.77931 | 0.80551 | 999.99 | 12 | 0.77931 | 0.78
2 | Jun | 999.99 | 999.99 | 0.11907 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.14453 | 999.99 | 999.99 | 0.77059 | 999.99 | 999.99 | 999.99 | 8 | 0.77059 | 0.77
3 | Jun | 0.03315 | 999.99 | 0.026928 | 999.99 | 999.99 | 0.07337 | 20 | 0 | 0.074097 | 0.80121 | 999.99 | 0.79786 | 999.99 | 999.99 | 0.7773 | 20 | 0.7773 | 0.78
4 | Jun | 0.03213 | 999.99 | 0.025279 | 0.026732 | 0.027752 | 999.99 | 0 | 0 | 0.03213 | 0.78914 | 999.99 | 0.78714 | 0.80651 | 0.79409 | 999.99 | 8 | 0.78714 | 0.79
5 | Jun | 999.99 | 999.99 | 0.028479 | 0.049089 | 999.99 | 999.99 | 12 | 0 | 0.050071 | 999.99 | 999.99 | 0.75999 | 0.77065 | 999.99 | 999.99 | 8 | 0.75999 | 0.76
6 | Jun | 0.028714 | 999.99 | 0.039019 | 999.99 | 0.023787 | 999.99 | 8 | 0 | 0.039019 | 0.74727 | 999.99 | 0.74868 | 999.99 | 0.74804 | 999.99 | 16 | 0.74804 | 0.75
7 | Jun | 999.99 | 999.99 | 0.057216 | 0.027536 | 0.026476 | 999.99 | 8 | 0 | 0.061986 | 999.99 | 999.99 | 0.71842 | 0.75304 | 0.7713 | 999.99 | 8 | 0.71842 | 0.72
8 | Jun | 999.99 | 999.99 | 0.029578 | 999.99 | 0.025515 | 999.99 | 8 | 0 | 0.031502 | 999.99 | 999.99 | 0.75451 | 999.99 | 0.77365 | 999.99 | 8 | 0.75451 | 0.75
9 | Jun | 999.99 | 999.99 | 0.025848 | 0.027615 | 0.024298 | 999.99 | 12 | 0 | 0.02789 | 999.99 | 999.99 | 0.75552 | 0.78202 | 0.77477 | 999.99 | 8 | 0.75552 | 0.76
10 | Jun | 999.99 | 999.99 | 0.025397 | 999.99 | 999.99 | 0.060612 | 20 | 0 | 0.061338 | 999.99 | 999.99 | 0.75811 | 999.99 | 999.99 | 0.75239 | 20 | 0.75239 | 0.75
11 | Jun | 0.027733 | 999.99 | 0.033268 | 999.99 | 0.025613 | 0.034014 | 20 | 0 | 0.035231 | 0.76294 | 999.99 | 0.74168 | 999.99 | 0.73979 | 0.76853 | 16 | 0.73979 | 0.74
12 | Jun | 999.99 | 999.99 | 0.063301 | 0.026143 | 0.022688 | 999.99 | 8 | 0 | 0.064871 | 999.99 | 999.99 | 0.72813 | 0.76258 | 0.79138 | 999.99 | 8 | 0.72813 | 0.73
13 | Jun | 999.99 | 999.99 | 0.057392 | 0.032444 | 0.028223 | 999.99 | 8 | 0 | 0.057412 | 999.99 | 999.99 | 0.74674 | 0.7882 | 0.81876 | 999.99 | 8 | 0.74674 | 0.75
14 | Jun | 999.99 | 999.99 | 0.053368 | 999.99 | 0.056823 | 999.99 | 16 | 0 | 0.057687 | 999.99 | 999.99 | 0.771 | 999.99 | 0.78349 | 999.99 | 8 | 0.771 | 0.77
15 | Jun | 999.99 | 999.99 | 999.99 | 0.050503 | 0.030893 | 999.99 | 12 | 0 | 0.050856 | 999.99 | 999.99 | 999.99 | 0.75917 | 0.75051 | 999.99 | 16 | 0.75051 | 0.75
16 | Jun | 999.99 | 999.99 | 0.065794 | 0.038902 | 0.036036 | 999.99 | 8 | 0 | 0.068699 | 999.99 | 999.99 | 0.77701 | 0.83531 | 0.8356 | 999.99 | 8 | 0.77701 | 0.78
17 | Jun | 999.99 | 999.99 | 0.064891 | 0.031874 | 0.030461 | 999.99 | 8 | 0 | 0.06491 | 999.99 | 999.99 | 0.81381 | 0.85203 | 0.8432 | 999.99 | 8 | 0.81381 | 0.81
18 | Jun | 999.99 | 999.99 | 999.99 | 999.99 | 0.039942 | 999.99 | 16 | 0 | 0.040982 | 999.99 | 999.99 | 999.99 | 999.99 | 0.81175 | 999.99 | 16 | 0.81175 | 0.81
19 | Jun | 999.99 | 999.99 | 999.99 | 0.045262 | 0.034485 | 999.99 | 12 | 0 | 0.048697 | 999.99 | 999.99 | 999.99 | 0.80051 | 0.82035 | 999.99 | 12 | 0.80051 | 0.8
20 | Jun | 999.99 | 999.99 | 0.071859 | 0.041414 | 0.040354 | 999.99 | 8 | 0 | 0.074509 | 999.99 | 999.99 | 0.77948 | 0.80168 | 0.80492 | 999.99 | 8 | 0.77948 | 0.78
21 | Jun | 999.99 | 999.99 | 999.99 | 0.064341 | 0.039216 | 999.99 | 12 | 0 | 0.066736 | 999.99 | 999.99 | 999.99 | 0.77424 | 0.80463 | 999.99 | 12 | 0.77424 | 0.77
22 | Jun | 999.99 | 999.99 | 0.058747 | 999.99 | 0.043927 | 999.99 | 8 | 0 | 0.061397 | 999.99 | 999.99 | 0.77766 | 999.99 | 0.78266 | 999.99 | 8 | 0.77766 | 0.78
23 | Jun | 999.99 | 999.99 | 0.061338 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.062574 | 999.99 | 999.99 | 0.76523 | 999.99 | 999.99 | 999.99 | 8 | 0.75 | 0.75
24 | Jun | 0.049246 | 999.99 | 0.044987 | 0.047794 | 999.99 | 999.99 | 0 | 0 | 0.051798 | 0.75946 | 999.99 | 0.78455 | 0.80033 | 999.99 | 999.99 | 0 | 0.77 | 0.77
25 | Jun | 999.99 | 0.064518 | 999.99 | 0.05433 | 0.062437 | 999.99 | 4 | 0 | 0.065067 | 999.99 | 0.75369 | 999.99 | 0.75257 | 0.73997 | 999.99 | 16 | 0.73997 | 0.74
26 | Jun | 999.99 | 999.99 | 0.075275 | 0.049914 | 999.99 | 0.049541 | 8 | 0 | 0.075275 | 999.99 | 999.99 | 0.68308 | 0.75139 | 999.99 | 0.74162 | 8 | 0.68308 | 0.68
27 | Jun | 999.99 | 999.99 | 0.066422 | 0.047833 | 0.045693 | 999.99 | 8 | 0 | 0.068679 | 999.99 | 999.99 | 0.74415 | 0.77218 | 0.80398 | 999.99 | 8 | 0.74415 | 0.74
28 | Jun | 999.99 | 999.99 | 0.051562 | 999.99 | 0.076433 | 999.99 | 16 | 0 | 0.078572 | 999.99 | 999.99 | 0.75422 | 999.99 | 0.79203 | 999.99 | 8 | 0.75422 | 0.75
29 | Jun | 999.99 | 999.99 | 999.99 | 0.055115 | 0.057059 | 999.99 | 16 | 0 | 0.057432 | 999.99 | 999.99 | 999.99 | 0.78673 | 0.83978 | 999.99 | 12 | 0.78673 | 0.79
30 | Jun | 999.99 | 999.99 | 0.069719 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.072899 | 999.99 | 999.99 | 0.80469 | 999.99 | 999.99 | 999.99 | 8 | 0.80469 | 0.8