## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Oct_25
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
2 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
3 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
4 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
5 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
6 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
7 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
8 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
9 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
10 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
11 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
12 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
13 | OFF | OFF | 0.02 | OFF | OFF | OFF | 0.02
14 | OFF | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02
15 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
16 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
17 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
18 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
19 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
20 | OFF | OFF | 0.02 | 0.03 | 0.02 | OFF | 0.03
21 | OFF | OFF | 0.02 | OFF | OFF | OFF | 0.02
22 | 0.02 | 0.02 | 0.02 | OFF | OFF | OFF | 0.02
23 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
24 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
25 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
26 | OFF | OFF | 0.02 | 0.03 | OFF | OFF | 0.03
27 | OFF | OFF | 0.03 | 0.02 | 0.02 | OFF | 0.03
28 | OFF | OFF | OFF | OFF | OFF | OFF | 0
29 | OFF | OFF | 0.03 | 0.02 | 0.02 | OFF | 0.03
30 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
31 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:11/03/2025
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Oct_25 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 12:00 | 0.83 | 111 | 92.13 | 16.7 | 7.42 | 13.9344 | YES | 831
2 / 8:00 | 0.81 | 111 | 89.91 | 16.4 | 7.39 | 14.0272 | YES | 840
3 / 8:00 | 0.82 | 111 | 91.02 | 16.4 | 7.44 | 14.3064 | YES | 840
4 / 12:00 | 0.84 | 111 | 93.24 | 16.3 | 7.39 | 14.1698 | YES | 875
5 / 8:00 | 0.75 | 111 | 83.25 | 16.1 | 7.35 | 14.0041 | YES | 872
6 / 8:00 | 0.72 | 111 | 79.92 | 16 | 7.26 | 13.5877 | YES | 878
7 / 8:00 | 0.74 | 111 | 82.14 | 15.9 | 7.32 | 14.0194 | YES | 871
8 / 8:00 | 0.79 | 111 | 87.69 | 15.9 | 7.28 | 13.8917 | YES | 873
9 / 8:00 | 0.84 | 111 | 93.24 | 15.5 | 7.36 | 14.7825 | YES | 834
10 / 8:00 | 0.85 | 111 | 94.35 | 15.3 | 7.34 | 14.8875 | YES | 833
11 / 12:00 | 0.82 | 111 | 91.02 | 15 | 7.39 | 15.42 | YES | 843
12 / 8:00 | 0.79 | 111 | 87.69 | 14.8 | 7.43 | 15.8062 | YES | 831
13 / 8:00 | 0.8 | 111 | 88.8 | 14.4 | 7.65 | 17.6289 | YES | 833
14 / 4:00 | 0.82 | 111 | 91.02 | 14.2 | 7.64 | 17.8395 | YES | 830
15 / 8:00 | 0.84 | 111 | 93.24 | 13.9 | 7.55 | 17.6441 | YES | 872
16 / 8:00 | 0.78 | 111 | 86.58 | 13.7 | 7.41 | 16.8635 | YES | 878
17 / 8:00 | 0.76 | 111 | 84.36 | 13.1 | 7.34 | 17.0635 | YES | 880
18 / 12:00 | 0.81 | 111 | 89.91 | 12.8 | 7.38 | 17.7672 | YES | 870
19 / 8:00 | 0.78 | 111 | 86.58 | 12.8 | 7.46 | 18.2376 | YES | 877
20 / 8:00 | 0.81 | 111 | 89.91 | 12.7 | 7.52 | 18.8341 | YES | 842
21 / 8:00 | 0.84 | 111 | 93.24 | 12.8 | 7.56 | 19.0522 | YES | 839
22 / 0:00 | 0.83 | 111 | 92.13 | 12.9 | 7.58 | 19.0446 | YES | 827
23 / 0:00 | 0.83 | 111 | 92.13 | 13 | 7.52 | 18.5044 | YES | 844
24 / 8:00 | 0.81 | 111 | 89.91 | 13 | 7.47 | 18.1249 | YES | 853
25 / 8:00 | 0.79 | 111 | 87.69 | 12.8 | 7.43 | 18.0572 | YES | 840
26 / 8:00 | 0.78 | 111 | 86.58 | 12.6 | 7.44 | 18.3457 | YES | 884
27 / 8:00 | 0.81 | 111 | 89.91 | 12.5 | 7.49 | 18.8759 | YES | 878
28 / 8:00 | 0.8 | 111 | 88.8 | 12.7 | 7.44 | 18.2656 | YES | 873
29 / 8:00 | 0.82 | 111 | 91.02 | 12.6 | 7.35 | 17.8269 | YES | 839
30 / 12:00 | 0.91 | 111 | 101.01 | 12.4 | 7.48 | 19.3006 | YES | 838
31 / 8:00 | 0.88 | 111 | 97.68 | 12.5 | 7.6 | 19.8136 | YES | 840
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Oct | 999.99 | 999.99 | 999.99 | 0.25853 | 0.25961 | 999.99 | 12 | 0 | 0.26071 | 999.99 | 999.99 | 999.99 | 0.8306 | 0.87017 | 999.99 | 12 | 0.8306 | 0.83
2 | Oct | 999.99 | 999.99 | 0.31353 | 0.27651 | 0.27694 | 999.99 | 8 | 0 | 0.3172 | 999.99 | 999.99 | 0.80993 | 0.85498 | 0.88201 | 999.99 | 8 | 0.80993 | 0.81
3 | Oct | 999.99 | 999.99 | 0.31477 | 0.29746 | 0.30162 | 999.99 | 8 | 0 | 0.31605 | 999.99 | 999.99 | 0.81588 | 0.86169 | 0.87447 | 999.99 | 8 | 0.81588 | 0.82
4 | Oct | 999.99 | 999.99 | 999.99 | 0.32782 | 0.328 | 999.99 | 16 | 0 | 0.33169 | 999.99 | 999.99 | 999.99 | 0.83248 | 0.84762 | 999.99 | 12 | 0.83248 | 0.83
5 | Oct | 999.99 | 999.99 | 0.37599 | 0.34918 | 0.35024 | 999.99 | 16 | 0 | 0.37953 | 999.99 | 999.99 | 0.74598 | 0.78973 | 0.82 | 999.99 | 8 | 0.74598 | 0.75
6 | Oct | 999.99 | 999.99 | 0.39666 | 0.37509 | 999.99 | 999.99 | 8 | 0 | 0.39739 | 999.99 | 999.99 | 0.71235 | 0.79032 | 999.99 | 999.99 | 8 | 0.71235 | 0.71
7 | Oct | 999.99 | 999.99 | 0.51514 | 0.39617 | 999.99 | 999.99 | 8 | 0 | 0.51514 | 999.99 | 999.99 | 0.73137 | 0.81652 | 999.99 | 999.99 | 8 | 0.73137 | 0.73
8 | Oct | 999.99 | 999.99 | 0.44956 | 0.41331 | 0.037057 | 999.99 | 8 | 0 | 0.44956 | 999.99 | 999.99 | 0.79373 | 0.86134 | 0.91286 | 999.99 | 8 | 0.79373 | 0.79
9 | Oct | 999.99 | 999.99 | 0.061652 | 0.036016 | 0.034053 | 999.99 | 8 | 0 | 0.062123 | 999.99 | 999.99 | 0.83272 | 0.91133 | 0.93583 | 999.99 | 8 | 0.83272 | 0.83
10 | Oct | 999.99 | 999.99 | 0.055665 | 0.03474 | 0.046793 | 999.99 | 8 | 0 | 0.056411 | 999.99 | 999.99 | 0.85816 | 0.88913 | 0.89561 | 999.99 | 8 | 0.85816 | 0.86
11 | Oct | 999.99 | 999.99 | 999.99 | 0.044516 | 0.049874 | 999.99 | 16 | 0 | 0.053741 | 999.99 | 999.99 | 999.99 | 0.82182 | 0.85615 | 999.99 | 12 | 0.82182 | 0.82
12 | Oct | 999.99 | 999.99 | 0.066638 | 0.043515 | 999.99 | 999.99 | 8 | 0 | 0.066755 | 999.99 | 999.99 | 0.7826 | 0.83342 | 999.99 | 999.99 | 8 | 0.7826 | 0.78
13 | Oct | 999.99 | 999.99 | 0.1416 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.144 | 999.99 | 999.99 | 0.79526 | 999.99 | 999.99 | 999.99 | 8 | 0.79526 | 0.8
14 | Oct | 999.99 | 0.056116 | 999.99 | 0.069248 | 0.044869 | 999.99 | 12 | 0 | 0.069543 | 999.99 | 0.81817 | 999.99 | 0.82271 | 0.87252 | 999.99 | 4 | 0.81817 | 0.82
15 | Oct | 999.99 | 999.99 | 0.073606 | 0.044143 | 0.048343 | 999.99 | 8 | 0 | 0.07553 | 999.99 | 999.99 | 0.82836 | 0.86493 | 0.85309 | 999.99 | 8 | 0.82836 | 0.83
16 | Oct | 999.99 | 999.99 | 0.073724 | 0.05062 | 0.051013 | 999.99 | 8 | 0 | 0.074686 | 999.99 | 999.99 | 0.77012 | 0.82218 | 0.83525 | 999.99 | 8 | 0.77012 | 0.77
17 | Oct | 999.99 | 999.99 | 0.12743 | 0.050404 | 0.054723 | 999.99 | 8 | 0 | 0.12743 | 999.99 | 999.99 | 0.76111 | 0.81699 | 0.83678 | 999.99 | 8 | 0.76111 | 0.76
18 | Oct | 999.99 | 999.99 | 999.99 | 0.059689 | 0.05645 | 999.99 | 12 | 0 | 0.059689 | 999.99 | 999.99 | 999.99 | 0.79897 | 0.84614 | 999.99 | 12 | 0.79897 | 0.8
19 | Oct | 999.99 | 999.99 | 0.086561 | 0.05647 | 0.055842 | 999.99 | 8 | 0 | 0.087013 | 999.99 | 999.99 | 0.77483 | 0.83619 | 0.86175 | 999.99 | 8 | 0.77483 | 0.77
20 | Oct | 999.99 | 999.99 | 0.084382 | 0.062908 | 0.060553 | 999.99 | 8 | 0 | 0.084382 | 999.99 | 999.99 | 0.8081 | 0.8717 | 0.88289 | 999.99 | 8 | 0.8081 | 0.81
21 | Oct | 999.99 | 999.99 | 0.086973 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.086973 | 999.99 | 999.99 | 0.84414 | 999.99 | 999.99 | 999.99 | 8 | 0.84414 | 0.84
22 | Oct | 0.0697 | 0.071251 | 0.068149 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.071604 | 0.83372 | 0.87812 | 0.89702 | 999.99 | 999.99 | 999.99 | 0 | 0.834 | 0.83
23 | Oct | 0.091802 | 999.99 | 0.0803 | 0.065833 | 999.99 | 999.99 | 8 | 0 | 0.0803 | 0.82441 | 999.99 | 0.84885 | 0.879 | 999.99 | 999.99 | 8 | 0.84885 | 0.85
24 | Oct | 999.99 | 999.99 | 0.089466 | 0.069504 | 999.99 | 999.99 | 8 | 0 | 0.090193 | 999.99 | 999.99 | 0.80533 | 0.84084 | 999.99 | 999.99 | 8 | 0.80533 | 0.81
25 | Oct | 999.99 | 999.99 | 0.097691 | 0.07602 | 999.99 | 999.99 | 8 | 0 | 0.097691 | 999.99 | 999.99 | 0.78278 | 0.82518 | 999.99 | 999.99 | 8 | 0.78278 | 0.78
26 | Oct | 999.99 | 999.99 | 0.10052 | 0.081791 | 999.99 | 999.99 | 8 | 0 | 0.10052 | 999.99 | 999.99 | 0.78337 | 0.84909 | 999.99 | 999.99 | 8 | 0.78337 | 0.78
27 | Oct | 999.99 | 999.99 | 0.1408 | 0.10093 | 0.082635 | 999.99 | 8 | 0 | 0.14449 | 999.99 | 999.99 | 0.81052 | 0.83236 | 0.86652 | 999.99 | 8 | 0.81052 | 0.81
28 | Oct | 999.99 | 999.99 | 999.99 | 999.99 | 999.99 | 999.99 | 0 | 0 | 0 | 999.99 | 999.99 | 999.99 | 999.99 | 999.99 | 999.99 | 8 | 0.8 | 0.8
29 | Oct | 999.99 | 999.99 | 0.10717 | 0.10064 | 0.0951 | 999.99 | 8 | 0 | 0.11016 | 999.99 | 999.99 | 0.81853 | 0.87553 | 0.91239 | 999.99 | 8 | 0.81853 | 0.82
30 | Oct | 999.99 | 999.99 | 999.99 | 0.10727 | 0.09879 | 999.99 | 12 | 0 | 0.10727 | 999.99 | 999.99 | 999.99 | 0.90603 | 0.92558 | 999.99 | 12 | 0.90603 | 0.91
31 | Oct | 999.99 | 999.99 | 0.12676 | 0.1004 | 0.10493 | 999.99 | 8 | 0 | 0.12676 | 999.99 | 999.99 | 0.8803 | 0.91381 | 0.92223 | 999.99 | 8 | 0.8803 | 0.88
Note on K1: Turbidity reading of the 4-hour interval having the HIGHEST recorded turbidity value.
Note on R1: HOUR of the 4-hour interval having the LOWEST recorded CL2 value.
Note on S1: CL2 reading of the 4-hour interval having the LOWEST recorded CL2 value.