## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Dec_25
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
2 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
3 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
4 | OFF | OFF | 0.02 | 0.03 | 0.02 | OFF | 0.03
5 | OFF | OFF | 0.02 | 0.02 | 0.04 | 0.02 | 0.040394
6 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.021
7 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
8 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
9 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
10 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
11 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
12 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
13 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
14 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
15 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
16 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
17 | OFF | OFF | OFF | OFF | 0.01 | 0.01 | 0.01
18 | 0.01 | OFF | 0.01 | OFF | OFF | OFF | 0.01
19 | OFF | OFF | 0.01 | 0.02 | 0.02 | 0.02 | 0.02
20 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
21 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
22 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
23 | OFF | OFF | 0.02 | 0.01 | 0.01 | OFF | 0.02
24 | OFF | OFF | 0.01 | 0.01 | 0.01 | OFF | 0.01
25 | OFF | OFF | 0.01 | 0.01 | OFF | OFF | 0.01
26 | OFF | OFF | 0.01 | 0.01 | 0.01 | OFF | 0.01
27 | OFF | OFF | 0.01 | 0.02 | OFF | OFF | 0.02
28 | OFF | OFF | 0.01 | 0.02 | OFF | OFF | 0.02
29 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
30 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
31 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:01/05/2026
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Dec_25 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 12:00 | 0.79 | 111 | 87.69 | 11.1 | 7.6 | 21.6191 | YES | 836
2 / 8:00 | 0.77 | 111 | 85.47 | 10.9 | 7.67 | 22.4013 | YES | 841
3 / 12:00 | 0.79 | 111 | 87.69 | 10.7 | 7.63 | 22.4326 | YES | 836
4 / 8:00 | 0.78 | 111 | 86.58 | 10.6 | 7.68 | 22.9572 | YES | 880
5 / 16:00 | 0.79 | 111 | 87.69 | 10.5 | 7.77 | 23.885 | YES | 785
6 / 16:00 | 0.74 | 111 | 82.14 | 10.7 | 7.69 | 22.7827 | YES | 785
7 / 12:00 | 0.72 | 111 | 79.92 | 11 | 7.44 | 20.4158 | YES | 784
8 / 8:00 | 0.74 | 111 | 82.14 | 11 | 7.39 | 20.1083 | YES | 786
9 / 12:00 | 0.78 | 111 | 86.58 | 11.1 | 7.33 | 19.6529 | YES | 824
10 / 8:00 | 0.75 | 111 | 83.25 | 11.1 | 7.37 | 19.8613 | YES | 830
11 / 12:00 | 0.74 | 111 | 82.14 | 11.2 | 7.37 | 19.7102 | YES | 829
12 / 8:00 | 0.72 | 111 | 79.92 | 11.2 | 7.25 | 18.866 | YES | 827
13 / 12:00 | 0.72 | 111 | 79.92 | 11 | 7.2 | 18.785 | YES | 828
14 / 12:00 | 0.72 | 111 | 79.92 | 10.8 | 7.22 | 19.1622 | YES | 785
15 / 8:00 | 0.74 | 111 | 82.14 | 10.8 | 7.25 | 19.4054 | YES | 786
16 / 8:00 | 0.72 | 111 | 79.92 | 10.8 | 7.25 | 19.3622 | YES | 769
17 / 16:00 | 0.72 | 111 | 79.92 | 10.8 | 7.16 | 18.769 | YES | 786
18 / 8:00 | 0.7 | 111 | 77.7 | 10.7 | 7.1 | 18.4631 | YES | 792
19 / 8:00 | 0.66 | 111 | 73.26 | 10.6 | 7.07 | 18.3107 | YES | 834
20 / 12:00 | 0.85 | 111 | 94.35 | 10.5 | 7.11 | 19.0833 | YES | 832
21 / 12:00 | 0.97 | 111 | 107.67 | 10.6 | 7.18 | 19.6863 | YES | 829
22 / 12:00 | 1.03 | 111 | 114.33 | 10.7 | 7.5 | 22.019 | YES | 828
23 / 8:00 | 1.05 | 111 | 116.55 | 10.6 | 7.56 | 22.6895 | YES | 826
24 / 8:00 | 1.05 | 111 | 116.55 | 10.5 | 7.66 | 23.6622 | YES | 790
25 / 8:00 | 1.04 | 111 | 115.44 | 10.2 | 7.59 | 23.5209 | YES | 790
26 / 16:00 | 0.99 | 111 | 109.89 | 10.4 | 7.62 | 23.3253 | YES | 793
27 / 8:00 | 0.96 | 111 | 106.56 | 10.2 | 7.59 | 23.3079 | YES | 784
28 / 8:00 | 0.96 | 111 | 106.56 | 10.1 | 7.62 | 23.7137 | YES | 790
29 / 16:00 | 0.93 | 111 | 103.23 | 9.9 | 7.74 | 24.9925 | YES | 826
30 / 8:00 | 0.9 | 111 | 99.9 | 9.7 | 7.64 | 24.3598 | YES | 823
31 / 12:00 | 0.89 | 111 | 98.79 | 9.6 | 7.67 | 24.7574 | YES | 825
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Dec | 999.99 | 999.99 | 999.99 | 0.07977 | 0.056411 | 999.99 | 12 | 0 | 0.082007 | 999.99 | 999.99 | 999.99 | 0.78967 | 0.79638 | 999.99 | 12 | 0.78967 | 0.79
2 | Dec | 999.99 | 999.99 | 0.089702 | 0.05806 | 0.052642 | 999.99 | 8 | 0 | 0.090153 | 999.99 | 999.99 | 0.76935 | 0.78673 | 0.81028 | 999.99 | 8 | 0.76935 | 0.77
3 | Dec | 999.99 | 999.99 | 999.99 | 0.033347 | 0.021765 | 999.99 | 12 | 0 | 0.036291 | 999.99 | 999.99 | 999.99 | 0.79738 | 0.80751 | 999.99 | 12 | 0.79738 | 0.8
4 | Dec | 999.99 | 999.99 | 0.066108 | 0.024278 | 0.024199 | 999.99 | 8 | 0 | 0.069307 | 999.99 | 999.99 | 0.7826 | 0.80757 | 0.82318 | 999.99 | 8 | 0.7826 | 0.78
5 | Dec | 999.99 | 999.99 | 0.037861 | 0.032601 | 0.035604 | 0.031541 | 8 | 0 | 0.040394 | 999.99 | 999.99 | 0.78879 | 0.79638 | 0.79385 | 0.80316 | 16 | 0.79 | 0.79
6 | Dec | 999.99 | 999.99 | 0.050483 | 0.020058 | 0.021569 | 0.020784 | 8 | 0 | 0.054958 | 999.99 | 999.99 | 0.78561 | 0.77018 | 0.74068 | 0.7445 | 16 | 0.74068 | 0.74
7 | Dec | 999.99 | 999.99 | 999.99 | 0.033406 | 999.99 | 999.99 | 12 | 0 | 0.033445 | 999.99 | 999.99 | 999.99 | 0.72542 | 999.99 | 999.99 | 12 | 0.72542 | 0.73
8 | Dec | 999.99 | 999.99 | 0.053624 | 0.035898 | 0.038725 | 999.99 | 8 | 0 | 0.053859 | 999.99 | 999.99 | 0.74115 | 0.7799 | 0.81399 | 999.99 | 8 | 0.74115 | 0.74
9 | Dec | 999.99 | 999.99 | 999.99 | 0.058923 | 999.99 | 999.99 | 12 | 0 | 0.059316 | 999.99 | 999.99 | 999.99 | 0.77442 | 999.99 | 999.99 | 12 | 0.77442 | 0.77
10 | Dec | 999.99 | 999.99 | 0.057805 | 0.048481 | 0.032503 | 0.031973 | 8 | 0 | 0.059571 | 999.99 | 999.99 | 0.76111 | 0.77925 | 0.81252 | 0.80215 | 8 | 0.76111 | 0.76
11 | Dec | 999.99 | 999.99 | 999.99 | 0.065008 | 999.99 | 999.99 | 12 | 0 | 0.073056 | 999.99 | 999.99 | 999.99 | 0.7395 | 999.99 | 999.99 | 12 | 0.7395 | 0.74
12 | Dec | 999.99 | 999.99 | 0.043259 | 0.040865 | 0.045792 | 999.99 | 16 | 0 | 0.04799 | 999.99 | 999.99 | 0.72124 | 0.74627 | 0.74998 | 999.99 | 8 | 0.72124 | 0.72
13 | Dec | 999.99 | 999.99 | 999.99 | 0.051072 | 0.045713 | 999.99 | 12 | 0 | 0.05115 | 999.99 | 999.99 | 999.99 | 0.71524 | 0.73043 | 999.99 | 12 | 0.71524 | 0.72
14 | Dec | 999.99 | 999.99 | 0.061299 | 0.046753 | 0.04587 | 999.99 | 8 | 0 | 0.066383 | 999.99 | 999.99 | 0.72054 | 0.72802 | 0.75846 | 999.99 | 12 | 0.72054 | 0.72
15 | Dec | 999.99 | 999.99 | 0.062417 | 0.047794 | 0.045419 | 999.99 | 8 | 0 | 0.066814 | 999.99 | 999.99 | 0.7382 | 0.74821 | 0.7501 | 999.99 | 8 | 0.7382 | 0.74
16 | Dec | 999.99 | 999.99 | 0.06228 | 0.050463 | 999.99 | 999.99 | 8 | 0 | 0.066127 | 999.99 | 999.99 | 0.72001 | 0.7289 | 999.99 | 999.99 | 8 | 0.72001 | 0.72
17 | Dec | 999.99 | 999.99 | 999.99 | 999.99 | 0.076963 | 0.061887 | 16 | 0 | 0.078965 | 999.99 | 999.99 | 999.99 | 999.99 | 0.70852 | 0.73432 | 16 | 0.70852 | 0.71
18 | Dec | 0.058609 | 999.99 | 0.076177 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.077434 | 0.74445 | 999.99 | 0.69586 | 999.99 | 999.99 | 999.99 | 8 | 0.69586 | 0.7
19 | Dec | 999.99 | 999.99 | 0.10413 | 0.078454 | 0.068483 | 0.070387 | 8 | 0 | 0.10833 | 999.99 | 999.99 | 0.65747 | 0.66925 | 0.79786 | 0.826 | 8 | 0.65747 | 0.66
20 | Dec | 999.99 | 999.99 | 999.99 | 0.073645 | 0.071094 | 999.99 | 12 | 0 | 0.076963 | 999.99 | 999.99 | 999.99 | 0.84338 | 0.92199 | 999.99 | 12 | 0.84338 | 0.84
21 | Dec | 999.99 | 999.99 | 999.99 | 0.081634 | 0.073155 | 999.99 | 12 | 0 | 0.085089 | 999.99 | 999.99 | 999.99 | 0.97434 | 1.0262 | 999.99 | 12 | 0.97434 | 0.97
22 | Dec | 999.99 | 999.99 | 999.99 | 0.10921 | 999.99 | 999.99 | 12 | 0 | 0.11122 | 999.99 | 999.99 | 999.99 | 1.0325 | 999.99 | 999.99 | 12 | 1.0325 | 1.03
23 | Dec | 999.99 | 999.99 | 0.11648 | 0.080555 | 0.076452 | 999.99 | 8 | 0 | 0.11653 | 999.99 | 999.99 | 1.0392 | 1.0833 | 1.0785 | 999.99 | 8 | 1.0392 | 1.04
24 | Dec | 999.99 | 999.99 | 0.094825 | 0.081634 | 0.079161 | 999.99 | 8 | 0 | 0.094825 | 999.99 | 999.99 | 1.0471 | 1.0638 | 1.0697 | 999.99 | 8 | 1.0471 | 1.05
25 | Dec | 999.99 | 999.99 | 0.11365 | 0.08346 | 999.99 | 999.99 | 8 | 0 | 0.11381 | 999.99 | 999.99 | 1.0361 | 1.0459 | 999.99 | 999.99 | 8 | 1.0361 | 1.04
26 | Dec | 999.99 | 999.99 | 0.28588 | 0.10774 | 0.098358 | 999.99 | 8 | 0 | 0.28588 | 999.99 | 999.99 | 1 | 0.9936 | 0.99336 | 999.99 | 16 | 0.99336 | 0.99
27 | Dec | 999.99 | 999.99 | 0.14578 | 0.10393 | 999.99 | 999.99 | 8 | 0 | 0.14578 | 999.99 | 999.99 | 0.96928 | 0.97929 | 999.99 | 999.99 | 8 | 0.96928 | 0.97
28 | Dec | 999.99 | 999.99 | 0.15089 | 0.11909 | 999.99 | 999.99 | 8 | 0 | 0.15522 | 999.99 | 999.99 | 0.95744 | 0.97169 | 999.99 | 999.99 | 8 | 0.95744 | 0.96
29 | Dec | 999.99 | 999.99 | 0.13781 | 0.12617 | 0.13145 | 999.99 | 8 | 0 | 0.14152 | 999.99 | 999.99 | 0.94201 | 0.94637 | 0.93389 | 999.99 | 16 | 0.93389 | 0.93
30 | Dec | 999.99 | 999.99 | 0.18033 | 0.15022 | 0.14725 | 999.99 | 8 | 0 | 0.18035 | 999.99 | 999.99 | 0.89708 | 0.91787 | 0.91186 | 999.99 | 8 | 0.89708 | 0.9
31 | Dec | 999.99 | 999.99 | 999.99 | 0.17723 | 0.16198 | 999.99 | 12 | 0 | 0.17933 | 999.99 | 999.99 | 999.99 | 0.89284 | 0.89526 | 999.99 | 12 | 0.89284 | 0.89
Note on K1: Turbidity reading of the 4-hour interval having the HIGHEST recorded turbidity value.
Note on R1: HOUR of the 4-hour interval having the LOWEST recorded CL2 value.
Note on S1: CL2 reading of the 4-hour interval having the LOWEST recorded CL2 value.