## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Jan_26
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
2 | OFF | OFF | 0.01 | OFF | 0.02 | OFF | 0.02
3 | OFF | OFF | 0.02 | 0.01 | 0.01 | OFF | 0.02
4 | OFF | OFF | OFF | 0.01 | 0.01 | OFF | 0.01
5 | OFF | OFF | 0.01 | 0.01 | OFF | OFF | 0.01
6 | OFF | OFF | 0.01 | 0.02 | 0.02 | OFF | 0.02
7 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
8 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
9 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
10 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
11 | OFF | OFF | 0.02 | 0.02 | 0.01 | OFF | 0.02
12 | OFF | OFF | 0.01 | 0.01 | 0.01 | OFF | 0.01
13 | OFF | OFF | 0.01 | OFF | OFF | 0.01 | 0.01
14 | OFF | OFF | 0.01 | 0.01 | 0.01 | OFF | 0.01
15 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
16 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
17 | OFF | OFF | 0.02 | 0.022237 | 0.02 | OFF | 0.02
18 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
19 | OFF | OFF | 0.02 | OFF | OFF | OFF | 0.02
20 | 0.02 | OFF | 0.024553 | 0.023198 | OFF | OFF | 0.02
21 | OFF | OFF | 0.02 | OFF | OFF | 0.02 | 0.021
22 | OFF | OFF | 0.02 | OFF | 0.02 | 0.01888 | 0.02
23 | 0.024945 | OFF | 0.02 | 0.023611 | 0.02 | OFF | 0.02
24 | OFF | OFF | OFF | 0.02 | 0.023728 | OFF | 0.02
25 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
26 | OFF | OFF | 0.02 | OFF | OFF | OFF | 0.02
27 | 0.02 | OFF | OFF | 0.02 | 0.025907 | 0.028243 | 0.03
28 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
29 | OFF | OFF | 0.02 | OFF | OFF | OFF | 0.02
30 | 0.02 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02
31 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Zachary J Dues
[5 empty] | SIGNATURE: Zachary J Dues |  |  | DATE:02/02/2026
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #: 269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Jan_26 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 8:00 | 0.88 | 111 | 97.68 | 9.5 | 7.79 | 25.9832 | YES | 826
2 / 16:00 | 0.86 | 111 | 95.46 | 9.5 | 7.68 | 24.9265 | YES | 787
3 / 8:00 | 0.83 | 111 | 92.13 | 9.5 | 7.61 | 24.2307 | YES | 783
4 / 12:00 | 0.82 | 111 | 91.02 | 9.5 | 7.52 | 23.4433 | YES | 793
5 / 8:00 | 0.8 | 111 | 88.8 | 9.3 | 7.54 | 23.8715 | YES | 785
6 / 8:00 | 0.77 | 111 | 85.47 | 9.2 | 7.43 | 23.0345 | YES | 789
7 / 8:00 | 0.77 | 111 | 85.47 | 9.1 | 7.49 | 23.6852 | YES | 829
8 / 8:00 | 0.75 | 111 | 83.25 | 9 | 7.44 | 23.3716 | YES | 824
9 / 12:00 | 0.75 | 111 | 83.25 | 9 | 7.35 | 22.6404 | YES | 828
10 / 8:00 | 0.74 | 111 | 82.14 | 9 | 7.31 | 22.2983 | YES | 830
11 / 8:00 | 0.72 | 111 | 79.92 | 9 | 7.3 | 22.1698 | YES | 783
12 / 8:00 | 0.71 | 111 | 78.81 | 9.1 | 7.44 | 23.1118 | YES | 780
13 / 8:00 | 0.71 | 111 | 78.81 | 9.1 | 7.42 | 22.9491 | YES | 778
14 / 8:00 | 0.74 | 111 | 82.14 | 9.1 | 7.3 | 22.0738 | YES | 786
15 / 12:00 | 0.74 | 111 | 82.14 | 9.3 | 7.33 | 22.0154 | YES | 787
16 / 8:00 | 0.72 | 111 | 79.92 | 9.2 | 7.18 | 20.978 | YES | 779
17 / 8:00 | 0.81 | 111 | 89.91 | 9.2 | 7.14 | 20.8969 | YES | 823
18 / 8:00 | 0.88 | 111 | 97.68 | 9 | 7.23 | 22.0253 | YES | 819
19 / 8:00 | 0.88 | 111 | 97.68 | 9 | 7.44 | 23.7198 | YES | 826
20 / 8:00 | 0.87 | 111 | 96.57 | 8.9 | 7.53 | 24.6251 | YES | 824
21 / 20:00 | 0.86 | 111 | 95.46 | 8.8 | 7.53 | 24.7617 | YES | 820
22 / 8:00 | 0.85 | 111 | 94.35 | 8.7 | 7.55 | 25.077 | YES | 784
23 / 8:00 | 0.85 | 111 | 94.35 | 8.4 | 7.46 | 24.778 | YES | 783
24 / 12:00 | 0.85 | 111 | 94.35 | 8.2 | 7.41 | 24.6684 | YES | 784
25 / 8:00 | 0.85 | 111 | 94.35 | 8 | 7.46 | 25.4494 | YES | 781
26 / 8:00 | 0.86 | 111 | 95.46 | 7.9 | 7.56 | 26.5831 | YES | 773
27 / 12:00 | 0.82 | 111 | 91.02 | 7.9 | 7.55 | 26.3666 | YES | 780
28 / 12:00 | 0.79 | 111 | 87.69 | 8 | 7.43 | 25.0064 | YES | 824
29 / 8:00 | 0.78 | 111 | 86.58 | 8 | 7.42 | 24.8891 | YES | 834
30 / 8:00 | 0.78 | 111 | 86.58 | 8 | 7.33 | 24.1057 | YES | 879
31 / 8:00 | 0.79 | 111 | 87.69 | 8.5 | 7.31 | 23.1797 | YES | 878
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Jan | 999.99 | 999.99 | 0.36145 | 0.18131 | 999.99 | 999.99 | 8 | 0 | 0.36145 | 999.99 | 999.99 | 0.86817 | 0.88636 | 999.99 | 999.99 | 8 | 0.86817 | 0.87
2 | Jan | 999.99 | 999.99 | 0.19639 | 999.99 | 0.20681 | 999.99 | 16 | 0 | 0.20893 | 999.99 | 999.99 | 0.86911 | 999.99 | 0.85757 | 999.99 | 16 | 0.85757 | 0.86
3 | Jan | 999.99 | 999.99 | 0.25251 | 0.22593 | 0.030442 | 999.99 | 8 | 0 | 0.25733 | 999.99 | 999.99 | 0.83955 | 0.83407 | 0.84526 | 999.99 | 12 | 0.83407 | 0.83
4 | Jan | 999.99 | 999.99 | 999.99 | 0.044398 | 0.028871 | 999.99 | 12 | 0 | 0.047853 | 999.99 | 999.99 | 999.99 | 0.81741 | 0.82306 | 999.99 | 12 | 0.81741 | 0.82
5 | Jan | 999.99 | 999.99 | 0.05433 | 0.033445 | 999.99 | 999.99 | 8 | 0 | 0.057785 | 999.99 | 999.99 | 0.80598 | 0.80245 | 999.99 | 999.99 | 8 | 0.80245 | 0.8
6 | Jan | 999.99 | 999.99 | 0.067678 | 0.030186 | 0.036271 | 999.99 | 8 | 0 | 0.0697 | 999.99 | 999.99 | 0.78101 | 0.79026 | 0.79521 | 999.99 | 8 | 0.78101 | 0.78
7 | Jan | 999.99 | 999.99 | 0.05168 | 0.035153 | 999.99 | 999.99 | 8 | 0 | 0.052171 | 999.99 | 999.99 | 0.77324 | 0.77412 | 999.99 | 999.99 | 8 | 0.77324 | 0.77
8 | Jan | 999.99 | 999.99 | 0.062947 | 0.034623 | 999.99 | 999.99 | 8 | 0 | 0.065617 | 999.99 | 999.99 | 0.76087 | 0.764 | 999.99 | 999.99 | 8 | 0.76087 | 0.76
9 | Jan | 999.99 | 999.99 | 999.99 | 0.043181 | 999.99 | 999.99 | 12 | 0 | 0.044339 | 999.99 | 999.99 | 999.99 | 0.75593 | 999.99 | 999.99 | 12 | 0.75593 | 0.76
10 | Jan | 999.99 | 999.99 | 0.07602 | 0.042003 | 0.041826 | 999.99 | 8 | 0 | 0.079887 | 999.99 | 999.99 | 0.74185 | 0.74533 | 0.75563 | 999.99 | 8 | 0.74185 | 0.74
11 | Jan | 999.99 | 999.99 | 0.079927 | 0.045615 | 0.041866 | 999.99 | 8 | 0 | 0.083028 | 999.99 | 999.99 | 0.72154 | 0.73573 | 0.74238 | 999.99 | 8 | 0.72154 | 0.72
12 | Jan | 999.99 | 999.99 | 0.064812 | 0.04481 | 0.043024 | 999.99 | 8 | 0 | 0.064812 | 999.99 | 999.99 | 0.7127 | 0.72978 | 0.7352 | 999.99 | 8 | 0.7127 | 0.71
13 | Jan | 999.99 | 999.99 | 0.071309 | 999.99 | 999.99 | 0.062496 | 8 | 0 | 0.071309 | 999.99 | 999.99 | 0.70976 | 999.99 | 999.99 | 0.71959 | 8 | 0.70976 | 0.71
14 | Jan | 999.99 | 999.99 | 0.059218 | 0.055214 | 0.056627 | 999.99 | 8 | 0 | 0.061142 | 999.99 | 999.99 | 0.7246 | 0.7332 | 0.73608 | 999.99 | 8 | 0.74 | 0.74
15 | Jan | 999.99 | 999.99 | 999.99 | 0.063046 | 0.025377 | 999.99 | 12 | 0 | 0.064361 | 999.99 | 999.99 | 999.99 | -0.74435 | 0.73396 | 999.99 | 12 | -0.74435 | -0.74
16 | Jan | 999.99 | 999.99 | 0.050071 | 0.026535 | 0.027831 | 999.99 | 8 | 0 | 0.054055 | 999.99 | 999.99 | 0.73549 | 0.77242 | 0.79209 | 999.99 | 8 | 0.73549 | 0.74
17 | Jan | 999.99 | 999.99 | 0.051091 | 0.022237 | 0.026633 | 999.99 | 8 | 0 | 0.053054 | 999.99 | 999.99 | 0.80769 | 0.86834 | 0.89696 | 999.99 | 8 | 0.80769 | 0.81
18 | Jan | 999.99 | 999.99 | 0.036154 | 0.020882 | 0.022884 | 999.99 | 8 | 0 | 0.040256 | 999.99 | 999.99 | 0.87953 | 0.88819 | 0.90144 | 999.99 | 8 | 0.87953 | 0.88
19 | Jan | 999.99 | 999.99 | 0.054919 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.055763 | 999.99 | 999.99 | 0.88042 | 999.99 | 999.99 | 999.99 | 8 | 0.88042 | 0.88
20 | Jan | 0.039805 | 999.99 | 0.024553 | 0.023198 | 999.99 | 999.99 | 0 | 0 | 0.044633 | 0.88142 | 999.99 | 0.86929 | 0.87358 | 999.99 | 999.99 | 8 | 0.86929 | 0.87
21 | Jan | 999.99 | 999.99 | 0.042788 | 999.99 | 999.99 | 0.032247 | 8 | 0 | 0.04532 | 999.99 | 999.99 | 0.86193 | 999.99 | 999.99 | 0.85763 | 20 | 0.85763 | 0.86
22 | Jan | 999.99 | 999.99 | 0.044123 | 999.99 | 0.028734 | 0.01888 | 8 | 0 | 0.047754 | 999.99 | 999.99 | 0.84767 | 999.99 | 0.8674 | 0.87618 | 8 | 0.84767 | 0.85
23 | Jan | 0.024945 | 999.99 | 0.030481 | 0.023611 | 0.025731 | 999.99 | 8 | 0 | 0.03052 | 0.8631 | 999.99 | 0.85551 | 0.8591 | 0.86122 | 999.99 | 8 | 0.85551 | 0.86
24 | Jan | 999.99 | 999.99 | 999.99 | 0.031796 | 0.023728 | 999.99 | 12 | 0 | 0.032326 | 999.99 | 999.99 | 999.99 | 0.84067 | 0.86204 | 999.99 | 12 | 0.84067 | 0.84
25 | Jan | 999.99 | 999.99 | 0.053427 | 0.027144 | 999.99 | 999.99 | 8 | 0 | 0.057353 | 999.99 | 999.99 | 0.85091 | 0.86275 | 999.99 | 999.99 | 8 | 0.85091 | 0.85
26 | Jan | 999.99 | 999.99 | 0.067325 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.07074 | 999.99 | 999.99 | 0.85203 | 999.99 | 999.99 | 999.99 | 8 | 0.85203 | 0.85
27 | Jan | 0.057765 | 999.99 | 999.99 | 0.032189 | 0.025907 | 0.028243 | 0 | 0 | 0.058276 | 0.82424 | 999.99 | 999.99 | 0.82094 | 0.82377 | 0.82224 | 12 | 0.82094 | 0.82
28 | Jan | 999.99 | 999.99 | 0.02 | 0.02 | 999.99 | 999.99 | 0 | 0 | 0.02 | 999.99 | 999.99 | 0.79 | 0.79 | 999.99 | 999.99 | 12 | 0.79 | 0.79
29 | Jan | 999.99 | 999.99 | 0.047283 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.048756 | 999.99 | 999.99 | 0.77418 | 999.99 | 999.99 | 999.99 | 8 | 0.77418 | 0.77
30 | Jan | 0.036271 | 999.99 | 999.99 | 0.056116 | 0.035722 | 0.031266 | 12 | 0 | 0.074646 | 0.78431 | 999.99 | 999.99 | 0.77483 | 0.78826 | 0.80045 | 12 | 0.77483 | 0.77
31 | Jan | 999.99 | 999.99 | 0.040335 | 0.031698 | 0.036468 | 999.99 | 8 | 0 | 0.041198 | 999.99 | 999.99 | 0.78255 | 0.81464 | 0.81399 | 999.99 | 8 | 0.78255 | 0.78
Note on K1: Turbidity reading of the 4-hour interval having the HIGHEST recorded turbidity value.
Note on R1: HOUR of the 4-hour interval having the LOWEST recorded CL2 value.
Note on S1: CL2 reading of the 4-hour interval having the LOWEST recorded CL2 value.