## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Mar_26
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
2 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
3 | OFF | OFF | 0.02 | OFF | OFF | OFF | 0.02
4 | 0.02 | 0.02 | OFF | OFF | 0.02 | OFF | 0.02
5 | OFF | OFF | 0.02 | 0.02 | 0.03 | 0.02 | 0.03
6 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
7 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
8 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
9 | 0.02 | OFF | 0.02 | 0.02 | 0.03 | 0.04 | 0.04
10 | OFF | OFF | 0.08 | 0.02 | OFF | 0.02 | 0.08
11 | 0.02 | OFF | 0.02 | OFF | OFF | OFF | 0.02
12 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
13 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
14 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
15 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
16 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
17 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
18 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
19 | OFF | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02
20 | OFF | OFF | OFF | 0.02 | OFF | OFF | 0.02
21 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
22 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
23 | OFF | OFF | 0.02 | OFF | OFF | OFF | 0.02
24 | 0.02 | 0.02 | OFF | OFF | 0.02 | OFF | 0.02
25 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
26 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
27 | OFF | OFF | 0.02 | 0.05 | 0.02 | OFF | 0.05
28 | OFF | 0.02 | OFF | 0.02 | OFF | OFF | 0.02
29 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
30 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
31 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:04/01/2026
[5 empty] | PHONE #: (541)336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Mar_26 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 12:00 | 0.78 | 111 | 86.58 | 8.8 | 7.02 | 20.5024 | YES | 824
2 / 12:00 | 0.78 | 111 | 86.58 | 8.8 | 7.12 | 21.2316 | YES | 824
3 / 8:00 | 0.75 | 111 | 83.25 | 8.8 | 7.16 | 21.4587 | YES | 827
4 / 16:00 | 0.76 | 111 | 84.36 | 8.9 | 7.2 | 21.6435 | YES | 831
5 / 8:00 | 0.74 | 111 | 82.14 | 8.9 | 7.23 | 21.8233 | YES | 787
6 / 8:00 | 0.81 | 111 | 89.91 | 8.8 | 7.06 | 20.8608 | YES | 788
7 / 8:00 | 0.83 | 111 | 92.13 | 8.7 | 7.05 | 20.9719 | YES | 788
8 / 16:00 | 0.86 | 111 | 95.46 | 8.7 | 7.04 | 20.9693 | YES | 785
9 / 20:00 | 0.83 | 111 | 92.13 | 8.5 | 7.14 | 21.9308 | YES | 785
10 / 20:00 | 0.83 | 111 | 92.13 | 8.5 | 7.28 | 23.0397 | YES | 829
11 / 0:00 | 0.82 | 111 | 91.02 | 8.5 | 7.37 | 23.758 | YES | 822
12 / 8:00 | 0.81 | 111 | 89.91 | 8.6 | 7.16 | 21.8908 | YES | 832
13 / 12:00 | 0.85 | 111 | 94.35 | 8.9 | 7.03 | 20.6008 | YES | 835
14 / 12:00 | 0.85 | 111 | 94.35 | 8.9 | 7.13 | 21.334 | YES | 838
15 / 12:00 | 0.87 | 111 | 96.57 | 9.1 | 7.06 | 20.5929 | YES | 831
16 / 12:00 | 0.89 | 111 | 98.79 | 9.2 | 7.26 | 21.9919 | YES | 832
17 / 12:00 | 0.86 | 111 | 95.46 | 9.4 | 7.01 | 19.8224 | YES | 837
18 / 8:00 | 0.82 | 111 | 91.02 | 9.9 | 7.01 | 19.1028 | YES | 789
19 / 8:00 | 0.8 | 111 | 88.8 | 9.9 | 7 | 18.9946 | YES | 779
20 / 12:00 | 0.78 | 111 | 86.58 | 10.2 | 7.06 | 18.9767 | YES | 786
21 / 12:00 | 0.78 | 111 | 86.58 | 9.6 | 7 | 19.3252 | YES | 787
22 / 8:00 | 0.77 | 111 | 85.47 | 9.6 | 6.98 | 19.1705 | YES | 777
23 / 8:00 | 0.77 | 111 | 85.47 | 10 | 7.09 | 19.4038 | YES | 770
24 / 16:00 | 0.78 | 111 | 86.58 | 9.7 | 7.07 | 19.6715 | YES | 817
25 / 8:00 | 0.77 | 111 | 85.47 | 10.7 | 7.06 | 18.3522 | YES | 785
26 / 8:00 | 0.79 | 111 | 87.69 | 9.9 | 7.25 | 20.695 | YES | 791
27 / 8:00 | 0.8 | 111 | 88.8 | 9.6 | 7.04 | 19.6388 | YES | 827
28 / 4:00 | 0.83 | 111 | 92.13 | 9.8 | 7.16 | 20.2779 | YES | 823
29 / 12:00 | 0.86 | 111 | 95.46 | 9.9 | 7.31 | 21.3007 | YES | 828
30 / 8:00 | 0.86 | 111 | 95.46 | 10.3 | 7.43 | 21.639 | YES | 827
31 / 8:00 | 0.84 | 111 | 93.24 | 10 | 7.53 | 22.8108 | YES | 825
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Mar | 999.99 | 999.99 | 999.99 | 0.072232 | 0.065048 | 999.99 | 12 | 0 | 0.073213 | 999.99 | 999.99 | 999.99 | 0.78243 | 0.80887 | 999.99 | 12 | 0.78243 | 0.78
2 | Mar | 999.99 | 999.99 | 0.094433 | 0.067933 | 999.99 | 999.99 | 8 | 0 | 0.094433 | 999.99 | 999.99 | 0.78284 | 0.77248 | 999.99 | 999.99 | 12 | 0.77248 | 0.77
3 | Mar | 999.99 | 999.99 | 0.061691 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.061691 | 999.99 | 999.99 | 0.75069 | 999.99 | 999.99 | 999.99 | 8 | 0.75069 | 0.75
4 | Mar | 0.039353 | 0.038568 | 999.99 | 999.99 | 0.040845 | 999.99 | 16 | 0 | 0.042533 | 0.75098 | 0.76205 | 999.99 | 999.99 | 0.7564 | 999.99 | 16 | 0.7564 | 0.76
5 | Mar | 999.99 | 999.99 | 0.060494 | 0.039078 | 0.041611 | 0.041552 | 8 | 0 | 0.061024 | 999.99 | 999.99 | 0.74827 | 0.76971 | 0.79638 | 0.81193 | 8 | 0.74827 | 0.75
6 | Mar | 999.99 | 999.99 | 0.045929 | 0.043966 | 0.045144 | 0.043554 | 8 | 0 | 0.046302 | 999.99 | 999.99 | 0.8061 | 0.82123 | 0.83195 | 0.8366 | 8 | 0.8061 | 0.81
7 | Mar | 0.0443 | 999.99 | 0.045536 | 0.046302 | 0.045399 | 0.043829 | 8 | 0 | 0.04744 | 0.84891 | 999.99 | 0.8389 | 0.85091 | 0.86063 | 0.87223 | 8 | 0.8389 | 0.84
8 | Mar | 0.045674 | 999.99 | 0.045949 | 0.047637 | 0.04748 | 0.046596 | 20 | 0 | 0.049246 | 0.87476 | 999.99 | 0.86811 | 0.86728 | 0.8624 | 0.87252 | 16 | 0.8624 | 0.86
9 | Mar | 999.99 | 999.99 | 0.053525 | 0.052269 | 0.04854 | 0.053074 | 8 | 0 | 0.053702 | 999.99 | 999.99 | 0.85044 | 0.84779 | 0.85191 | 0.83219 | 20 | 0.83219 | 0.83
10 | Mar | 999.99 | 0.058531 | 0.063438 | 0.063477 | 999.99 | 999.99 | 8 | 0 | 0.067168 | 999.99 | 0.82206 | 0.82736 | 0.83713 | 999.99 | 999.99 | 20 | 0.83 | 0.83
11 | Mar | 0.068483 | 999.99 | 0.066441 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.066441 | 0.82506 | 999.99 | 0.8197 | 999.99 | 999.99 | 999.99 | 0 | 0.8197 | 0.82
13 | Mar | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | #VALUE!
14 | Mar | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | #VALUE!
15 | Mar | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | 12 | 0.87 | 0.87
16 | Mar | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | 12 | 0.89 | 0.89
17 | Mar | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | 12 | 0.86 | 0.86
18 | Mar | 999.99 | 999.99 | 0.13997 | 0.12708 | 999.99 | 999.99 | 8 | 0 | 0.14284 | 999.99 | 999.99 | 0.83437 | 0.83501 | 999.99 | 999.99 | 8 | 0.82 | 0.82
19 | Mar | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | 8 | 0.8 | 0.8
20 | Mar | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | #VALUE!
21 | Mar | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | #VALUE!
22 | Mar | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | 8 | 0.77 | 0.77
23 | Mar | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | 8 | 0.77 | 0.77
24 | Mar | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | 16 | 0.78 | 0.78
25 | Mar | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | 8 | 0.77 | 0.77
26 | Mar | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | ??? | #VALUE!
27 | Mar | 999.99 | 999.99 | 0.29726 | 999.99 | 999.99 | 999.99 | 8 | 0 | 0.30081 | 999.99 | 999.99 | 0.7968 | 999.99 | 999.99 | 999.99 | 8 | 0.7968 | 0.8
28 | Mar | 999.99 | 0.31591 | 999.99 | 999.99 | 999.99 | 999.99 | 4 | 0 | 0.31679 | 999.99 | 0.83077 | 999.99 | 999.99 | 999.99 | 999.99 | 4 | 0.83077 | 0.83
29 | Mar | 999.99 | 999.99 | 999.99 | 999.99 | 999.99 | 999.99 | 0 | 0 | 0 | 999.99 | 999.99 | 999.99 | 999.99 | 999.99 | 999.99 | 12 | 0.86 | 0.86
30 | Mar | 999.99 | 999.99 | 0.43741 | 0.43044 | 0.44656 | 999.99 | 16 | 0 | 0.44676 | 999.99 | 999.99 | 0.86405 | 0.87971 | 0.86817 | 999.99 | 8 | 0.86405 | 0.86
31 | Mar | 999.99 | 999.99 | 0.50794 | 0.50441 | 999.99 | 999.99 | 12 | 0 | 0.50816 | 999.99 | 999.99 | 0.84143 | 0.85256 | 999.99 | 999.99 | 8 | 0.84143 | 0.84
Note on K1: Turbidity reading of the 4-hour interval having the HIGHEST recorded turbidity value.
Note on R1: HOUR of the 4-hour interval having the LOWEST recorded CL2 value.
Note on S1: CL2 reading of the 4-hour interval having the LOWEST recorded CL2 value.