## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-01-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.049 | 0.051 | 0.047 | NIS | NIS | 0.057 | 0.057
2 | NIS | 0.051 | 0.051 | NIS | NIS | 0.07 | 0.07
3 | 0.047 | 0.057 | 0.043 | 0.047 | 0.076 | NIS | 0.076
4 | NIS | NIS | 0.064 | 0.043 | 0.041 | NIS | 0.064
5 | 0.041 | 0.045 | 0.047 | 0.043 | NIS | NIS | 0.047
6 | NIS | NIS | 0.066 | 0.047 | 0.057 | 0.041 | 0.066
7 | 0.047 | 0.043 | 0.047 | NIS | 0.12 | NIS | 0.12
8 | 0.045 | 0.045 | 0.046 | 0.047 | NIS | 0.041 | 0.05
9 | 0.039 | NIS | 0.041 | NIS | 0.041 | NIS | 0.04
10 | 0.047 | 0.039 | 0.041 | NIS | NIS | NIS | 0.05
11 | NIS | NIS | 0.045 | 0.087 | 0.039 | NIS | 0.087
12 | 0.055 | 0.057 | 0.039 | 0.045 | 0.045 | NIS | 0.06
13 | NIS | NIS | 0.039 | 0.037 | 0.035 | NIS | 0.04
14 | 0.037 | 0.037 | 0.041 | 0.037 | NIS | NIS | 0.04
15 | NIS | NIS | 0.035 | 0.039 | 0.158 | NIS | 0.158
16 | NIS | NIS | 0.045 | 0.041 | NIS | NIS | 0.045
17 | NIS | NIS | 0.057 | 0.046 | 0.078 | NIS | 0.078
18 | NIS | NIS | NIS | 0.053 | 0.047 | 0.043 | 0.05
19 | NIS | 0.045 | 0.051 | 0.066 | 0.045 | NIS | 0.07
20 | NIS | NIS | 0.07 | 0.068 | 0.055 | NIS | 0.07
21 | NIS | NIS | 0.06 | 0.055 | NIS | 0.053 | 0.06
22 | NIS | NIS | 0.052 | NIS | NIS | 0.051 | 0.05
23 | NIS | 0.055 | 0.055 | 0.055 | NIS | NIS | 0.055
24 | NIS | NIS | 0.053 | 0.053 | 0.045 | NIS | 0.05
25 | NIS | NIS | 0.043 | 0.041 | 0.062 | NIS | 0.062
26 | 0.045 | 0.07 | 0.043 | 0.043 | NIS | NIS | 0.07
27 | NIS | NIS | NIS | 0.045 | 0.043 | 0.043 | 0.05
28 | NIS | NIS | 0.045 | 0.043 | 0.043 | 0.043 | 0.05
29 | NIS | NIS | 0.045 | NIS | 0.041 | 0.043 | 0.05
30 | NIS | 0.041 | 0.043 | 0.049 | 0.041 | NIS | 0.05
31 | NIS | NIS | NIS | 0.045 | 0.041 | NIS | 0.045
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME:Anthony Rogers
[5 empty] | SIGNATURE: |  |  | DATE:2/2/2023
[5 empty] | PHONE #: ( 541) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2023-01-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.1 | 63 | 69.3 | 7.9 | 7.9 | 30.8929 | YES | 300
2 | 1.06 | 63 | 66.78 | 7.8 | 7.8 | 29.8588 | YES | 300
3 | 1.11 | 63 | 69.93 | 8 | 7.8 | 29.6281 | YES | 300
4 | 1.14 | 63 | 71.82 | 7.8 | 7.8 | 30.1376 | YES | 300
5 | 1.13 | 63 | 71.19 | 7.6 | 7.8 | 30.5141 | YES | 300
6 | 1.06 | 63 | 66.78 | 7.8 | 7.8 | 29.8588 | YES | 300
7 | 1.15 | 63 | 72.45 | 7.9 | 7.7 | 28.906 | YES | 300
8 | 1.15 | 63 | 72.45 | 7.8 | 7.7 | 29.1023 | YES | 300
9 | 0.95 | 63 | 59.85 | 7.8 | 7.8 | 29.48 | YES | 300
10 | 1.18 | 63 | 74.34 | 7.6 | 7.7 | 29.602 | YES | 300
11 | 0.77 | 63 | 48.51 | 8 | 7.7 | 27.4776 | YES | 300
12 | 1.11 | 63 | 69.93 | 7.9 | 7.7 | 28.7724 | YES | 300
13 | 0.8 | 63 | 50.4 | 7.9 | 7.7 | 27.7594 | YES | 300
14 | 1.11 | 63 | 69.93 | 7.8 | 7.7 | 28.9677 | YES | 300
15 | 1.06 | 63 | 66.78 | 8 | 7.7 | 28.4137 | YES | 300
16 | 1.05 | 63 | 66.15 | 8.2 | 7.7 | 28.0002 | YES | 300
17 | 0.95 | 63 | 59.85 | 8.2 | 7.8 | 28.6926 | YES | 300
18 | 1.09 | 63 | 68.67 | 8.1 | 7.8 | 29.3599 | YES | 300
19 | 0.88 | 63 | 55.44 | 8 | 7.7 | 27.8287 | YES | 300
20 | 0.91 | 63 | 57.33 | 8.1 | 7.8 | 28.7538 | YES | 300
21 | 0.95 | 63 | 59.85 | 7.7 | 7.8 | 29.6804 | YES | 300
22 | 0.88 | 63 | 55.44 | 7.4 | 7.7 | 28.9798 | YES | 300
23 | 0.92 | 63 | 57.96 | 7.3 | 7.8 | 30.3909 | YES | 300
24 | 0.7 | 63 | 44.1 | 8.1 | 7.6 | 26.1217 | YES | 300
25 | 1.24 | 63 | 78.12 | 7.7 | 7.6 | 28.5587 | YES | 300
26 | 1.2 | 63 | 75.6 | 6.9 | 7.7 | 31.1153 | YES | 300
27 | 1.28 | 63 | 80.64 | 7.2 | 7.7 | 30.7723 | YES | 300
28 | 1.22 | 63 | 76.86 | 7.2 | 7.7 | 30.5582 | YES | 300
29 | 1.1 | 63 | 69.3 | 7.3 | 7.7 | 29.931 | YES | 300
30 | 1.33 | 63 | 83.79 | 6.6 | 7.7 | 32.2429 | YES | 300
31 | 1.27 | 63 | 80.01 | 5.9 | 7.7 | 33.5853 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2