## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-02-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.041 | 0.041 | 0.043 | 0.045 | NIS | NIS | 0.05
2 | NIS | NIS | 0.053 | 0.05 | 0.049 | NIS | 0.05
3 | NIS | NIS | 0.04 | 0.045 | 0.049 | NIS | 0.05
4 | NIS | NIS | 0.04 | 0.04 | 0.07 | 0.04 | 0.07
5 | 0.043 | 0.04 | 0.04 | NIS | NIS | NIS | 0.04
6 | NIS | NIS | 0.04 | 0.04 | 0.04 | NIS | 0.04
7 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | NIS | 0.05
8 | NIS | NIS | 0.05 | 0.05 | 0.04 | NIS | 0.05
9 | NIS | NIS | 0.04 | 0.04 | 0.04 | NIS | 0.04
10 | NIS | 0.04 | 0.05 | NIS | NIS | NIS | 0.05
11 | NIS | NIS | 0.05 | 0.04 | 0.04 | NIS | 0.05
12 | 0.04 | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.05
13 | NIS | NIS | NIS | 0.06 | 0.04 | NIS | 0.06
14 | NIS | NIS | 0.064 | 0.137 | 0.03 | 0.03 | 0.14
15 | 0.03 | 0.04 | 0.04 | 0.04 | 0.15 | NIS | 0.15
16 | NIS | NIS | 0.05 | 0.05 | 0.05 | NIS | 0.05
17 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | NIS | 0.05
18 | NIS | NIS | 0.06 | 0.05 | 0.05 | NIS | 0.06
19 | NIS | NIS | 0.05 | 0.05 | 0.05 | NIS | 0.05
20 | NIS | NIS | 0.049 | NIS | 0.05 | NIS | 0.05
21 | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | NIS | 0.05
22 | NIS | NIS | 0.05 | 0.04 | 0.04 | NIS | 0.05
23 | NIS | NIS | 0.05 | 0.04 | 0.05 | 0.05 | 0.05
24 | 0.05 | 0.05 | 0.04 | 0.05 | 0.05 | NIS | 0.05
25 | NIS | NIS | 0.06 | NIS | 0.05 | 0.06 | 0.06
26 | 0.06 | 0.05 | 0.05 | 0.05 | NIS | NIS | 0.06
27 | NIS | NIS | NIS | 0.05 | 0.05 | 0.05 | 0.05
28 | 0.06 | 0.05 | 0.05 | 0.05 | 0.05 | NIS | 0.06
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony Rogers
[5 empty] | SIGNATURE: |  |  | DATE: 3/1/2013
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #: 6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2023-02-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.31 | 63 | 82.53 | 6 | 7.7 | 33.513 | YES | 300
2 | 1.2 | 63 | 75.6 | 6.5 | 7.7 | 31.9745 | YES | 300
3 | 1.29 | 63 | 81.27 | 5.7 | 7.7 | 34.128 | YES | 300
4 | 1.29 | 63 | 81.27 | 6.4 | 7.7 | 32.5334 | YES | 300
5 | 1.31 | 63 | 82.53 | 6.4 | 7.8 | 33.819 | YES | 300
6 | 1 | 63 | 63 | 6.3 | 7.8 | 32.8376 | YES | 300
7 | 1.33 | 63 | 83.79 | 6.9 | 7.7 | 31.5903 | YES | 300
8 | 1.31 | 63 | 82.53 | 6.6 | 7.8 | 33.3596 | YES | 300
9 | 1.05 | 63 | 66.15 | 7.1 | 7.8 | 31.2767 | YES | 300
10 | 1.37 | 63 | 86.31 | 7.1 | 7.8 | 32.4666 | YES | 300
11 | 1.36 | 63 | 85.68 | 7.2 | 7.8 | 32.2082 | YES | 300
12 | 1.31 | 63 | 82.53 | 7.4 | 7.8 | 31.5874 | YES | 300
13 | 1.17 | 63 | 73.71 | 7.5 | 7.7 | 29.7688 | YES | 300
14 | 0.97 | 63 | 61.11 | 8.2 | 7.7 | 27.7427 | YES | 300
15 | 1.31 | 63 | 82.53 | 7.3 | 7.8 | 31.8033 | YES | 300
16 | 1.25 | 63 | 78.75 | 8.1 | 7.7 | 28.8498 | YES | 300
17 | 1.21 | 63 | 76.23 | 7.3 | 8.7 | 43.7239 | YES | 300
18 | 1.06 | 63 | 66.78 | 7.5 | 7.8 | 30.473 | YES | 300
19 | 1.06 | 63 | 66.78 | 7.4 | 7.7 | 29.591 | YES | 300
20 | 1.1 | 63 | 69.3 | 7 | 7.7 | 30.5468 | YES | 300
21 | 1.26 | 63 | 79.38 | 7.8 | 7.8 | 30.561 | YES | 300
22 | 1.12 | 63 | 70.56 | 8.5 | 7.7 | 27.6621 | YES | 300
23 | 1.02 | 63 | 64.26 | 7.9 | 7.8 | 29.5197 | YES | 300
24 | 1.24 | 63 | 78.12 | 7.3 | 7.9 | 32.7119 | YES | 300
25 | 1.28 | 63 | 80.64 | 7.5 | 7.8 | 31.2635 | YES | 300
26 | 1.22 | 63 | 76.86 | 7.1 | 7.9 | 33.0843 | YES | 300
27 | 1.28 | 63 | 80.64 | 7.3 | 7.8 | 31.6922 | YES | 300
28 | 1.25 | 63 | 78.75 | 6.8 | 7.9 | 33.8888 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2