## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-03-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | NIS | 0.049 | 0.049 | 0.053 | NIS | 0.053
2 | 0.052 | 0.053 | 0.049 | 0.055 | 0.053 | NIS | 0.06
3 | NIS | NIS | 0.05 | 0.047 | 0.049 | NIS | 0.05
4 | 0.051 | 0.051 | 0.049 | NIS | NIS | 0.07 | 0.07
5 | 0.056 | 0.048 | 0.048 | 0.054 | 0.054 | NIS | 0.06
6 | NIS | NIS | 0.059 | 0.049 | 0.052 | 0.057 | 0.06
7 | 0.049 | 0.045 | 0.066 | 0.054 | 0.056 | NIS | 0.07
8 | NIS | NIS | 0.057 | 0.049 | 0.055 | 0.057 | 0.06
9 | 0.051 | 0.066 | 0.05 | 0.051 | 0.064 | NIS | 0.07
10 | NIS | NIS | 0.066 | 0.051 | 0.056 | NIS | 0.07
11 | NIS | NIS | 0.049 | 0.057 | 0.052 | NIS | 0.06
12 | NIS | NIS | 0.06 | 0.052 | 0.06 | 0.049 | 0.06
13 | 0.074 | 0.055 | 0.057 | 0.051 | 0.049 | 0.062 | 0.07
14 | 0.064 | 0.049 | 0.047 | NIS | NIS | NIS | 0.06
15 | NIS | NIS | 0.053 | 0.076 | 0.049 | NIS | 0.08
16 | 0.055 | 0.051 | 0.068 | 0.049 | 0.049 | NIS | 0.07
17 | NIS | NIS | NIS | 0.055 | 0.048 | NIS | 0.06
18 | 0.053 | 0.049 | 0.049 | 0.049 | 0.053 | NIS | 0.05
19 | NIS | NIS | 0.053 | 0.049 | 0.051 | NIS | 0.05
20 | 0.051 | 0.051 | 0.047 | 0.05 | 0.049 | NIS | 0.05
21 | NIS | NIS | 0.057 | 0.049 | 0.064 | NIS | 0.06
22 | 0.055 | 0.061 | 0.057 | 0.051 | 0.057 | NIS | 0.06
23 | NIS | NIS | 0.049 | 0.045 | 0.046 | NIS | 0.05
24 | 0.047 | 0.055 | 0.045 | NIS | NIS | NIS | 0.06
25 | NIS | NIS | NIS | NIS | NIS | NIS | NIS
26 | 0.057 | 0.068 | 0.047 | NIS | NIS | NIS | 0.07
27 | NIS | NIS | 0.045 | 0.043 | 0.045 | 0.053 | 0.05
28 | 0.049 | 0.053 | 0.047 | 0.059 | NIS | NIS | 0.06
29 | NIS | NIS | NIS | 0.072 | 0.051 | NIS | 0.07
30 | NIS | NIS | 0.049 | 0.053 | 0.047 | NIS | 0.05
31 | 0.053 | 0.049 | 0.051 | 0.049 | NIS | NIS | 0.05
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony Rogers
[5 empty] | SIGNATURE: |  |  | DATE:4/3/2023
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2023-03-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.24 | 63 | 78.12 | 7 | 7.8 | 32.1962 | YES | 300
2 | 1.27 | 63 | 80.01 | 7.1 | 7.9 | 33.2784 | YES | 300
3 | 1.1 | 63 | 69.3 | 7.6 | 7.9 | 31.53 | YES | 300
4 | 1.26 | 63 | 79.38 | 7 | 7.9 | 33.4675 | YES | 300
5 | 1.29 | 63 | 81.27 | 7 | 7.9 | 33.5853 | YES | 300
6 | 1.1 | 63 | 69.3 | 7.2 | 7.9 | 32.4014 | YES | 300
7 | 1.31 | 63 | 82.53 | 7.4 | 7.9 | 32.7563 | YES | 300
8 | 1.13 | 63 | 71.19 | 7.9 | 7.9 | 31.001 | YES | 300
9 | 1.14 | 63 | 71.82 | 7.4 | 7.9 | 32.1121 | YES | 300
10 | 1.26 | 63 | 79.38 | 7.5 | 7.8 | 31.1908 | YES | 300
11 | 1.34 | 63 | 84.42 | 7.6 | 7.8 | 31.2694 | YES | 300
12 | 1.08 | 63 | 68.04 | 7.6 | 7.9 | 31.4565 | YES | 300
13 | 1.21 | 63 | 76.23 | 8.2 | 7.8 | 29.5704 | YES | 300
14 | 1.31 | 63 | 82.53 | 8.2 | 7.8 | 29.9157 | YES | 300
15 | 1.16 | 63 | 73.08 | 8.6 | 7.9 | 29.6653 | YES | 300
16 | 1.29 | 63 | 81.27 | 8.1 | 7.9 | 31.1574 | YES | 300
17 | 1.43 | 63 | 90.09 | 8.3 | 7.9 | 31.2417 | YES | 300
18 | 1.39 | 63 | 87.57 | 8.5 | 7.9 | 30.6764 | YES | 300
19 | 1.22 | 63 | 76.86 | 8.9 | 7.9 | 29.2715 | YES | 300
20 | 1.37 | 63 | 86.31 | 8.8 | 8 | 31.0935 | YES | 300
21 | 1.35 | 63 | 85.05 | 9.1 | 7.9 | 29.3163 | YES | 300
22 | 1.33 | 63 | 83.79 | 9.6 | 8 | 29.3136 | YES | 300
23 | 1.15 | 63 | 72.45 | 9.1 | 7.9 | 28.6448 | YES | 300
24 | 1.22 | 63 | 76.86 | 9.8 | 8 | 28.5534 | YES | 300
25 | NIS | 63 | #VALUE! | 9.9 | 7.9 | #VALUE! | #VALUE! | NIS
26 | 1.19 | 63 | 74.97 | 10 | 8.1 | 29.1023 | YES | 300
27 | 0.85 | 63 | 53.55 | 10.1 | 8 | 26.812 | YES | 300
28 | 1.04 | 63 | 65.52 | 9.6 | 8.1 | 29.3857 | YES | 300
29 | 1.1 | 63 | 69.3 | 9.8 | 7.9 | 27.1663 | YES | 300
30 | 0.79 | 63 | 49.77 | 10.3 | 8 | 26.2722 | YES | 300
31 | 1.06 | 63 | 66.78 | 9.9 | 8.1 | 28.8619 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2