## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-04-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | NIS | 0.057 | 0.051 | 0.05 | 0.047 | 0.06
2 | 0.057 | 0.053 | NIS | NIS | NIS | 0.048 | 0.06
3 | NIS | NIS | 0.059 | 0.06 | 0.048 | NIS | 0.06
4 | 0.051 | 0.053 | 0.05 | NIS | NIS | NIS | 0.05
5 | NIS | NIS | 0.045 | 0.049 | 0.045 | NIS | 0.05
6 | 0.049 | 0.064 | 0.054 | NIS | NIS | NIS | 0.06
7 | NIS | NIS | NIS | 0.051 | 0.047 | NIS | 0.05
8 | NIS | NIS | 0.041 | NIS | NIS | 0.05 | 0.05
9 | NIS | NIS | 0.043 | NIS | NIS | 0.045 | 0.05
10 | 0.051 | 0.043 | 0.045 | NIS | 0.045 | NIS | 0.05
11 | NIS | NIS | 0.051 | 0.049 | 0.047 | NIS | 0.05
12 | NIS | NIS | 0.049 | 0.05 | 0.051 | NIS | 0.05
13 | 0.051 | 0.051 | 0.047 | NIS | NIS | NIS | 0.05
14 | NIS | NIS | 0.062 | 0.057 | 0.057 | NIS | 0.06
15 | NIS | NIS | 0.053 | 0.057 | 0.051 | NIS | 0.06
16 | 0.055 | 0.057 | 0.054 | 0.052 | 0.054 | NIS | 0.06
17 | NIS | NIS | 0.053 | 0.056 | 0.059 | NIS | 0.06
18 | NIS | NIS | 0.055 | 0.055 | 0.09 | NIS | 0.09
19 | NIS | NIS | 0.057 | 0.055 | 0.062 | NIS | 0.06
20 | 0.053 | 0.053 | 0.058 | 0.043 | NIS | NIS | 0.06
21 | NIS | NIS | 0.037 | 0.039 | 0.041 | 0.041 | 0.041
22 | 0.041 | 0.043 | 0.039 | NIS | NIS | NIS | 0.04
23 | NIS | NIS | 0.041 | NIS | NIS | 0.041 | 0.04
24 | 0.039 | 0.049 | 0.041 | NIS | NIS | NIS | 0.05
25 | NIS | NIS | 0.043 | 0.052 | 0.045 | NIS | 0.05
26 | NIS | NIS | 0.041 | 0.041 | 0.05 | NIS | 0.05
27 | 0.051 | 0.051 | 0.05 | NIS | NIS | NIS | 0.05
28 | NIS | NIS | 0.05 | 0.047 | 0.045 | 0.049 | 0.05
29 | 0.043 | NIS | NIS | 0.041 | 0.045 | 0.041 | 0.05
30 | 0.041 | 0.039 | 0.039 | 0.043 | 0.046 | NIS | 0.05
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony Rogers
[5 empty] | SIGNATURE: |  |  | DATE: 5/2/2023
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #: 6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2023-04-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.07 | 63 | 67.41 | 9.9 | 8.2 | 29.9574 | YES | 300
2 | 1 | 63 | 63 | 10.2 | 8.2 | 29.1171 | YES | 300
3 | 0.96 | 63 | 60.48 | 10.6 | 8.1 | 27.214 | YES | 300
4 | 1.05 | 63 | 66.15 | 10.2 | 8 | 27.2529 | YES | 300
5 | 1.08 | 63 | 68.04 | 10.4 | 8 | 26.9817 | YES | 300
6 | 1.04 | 63 | 65.52 | 10.2 | 8 | 27.2215 | YES | 300
7 | 1.07 | 63 | 67.41 | 10.5 | 7.8 | 24.9249 | YES | 300
8 | 0.9 | 63 | 56.7 | 10.6 | 7.8 | 24.283 | YES | 300
9 | 0.91 | 63 | 57.33 | 10.3 | 7.8 | 24.8021 | YES | 300
10 | 1.2 | 63 | 75.6 | 11 | 8 | 26.2759 | YES | 300
11 | 1.12 | 63 | 70.56 | 10.6 | 7.8 | 24.9009 | YES | 300
12 | 1.13 | 63 | 71.19 | 10.7 | 7.9 | 25.6618 | YES | 300
13 | 1.13 | 63 | 71.19 | 10.9 | 7.9 | 25.3205 | YES | 300
14 | 0.92 | 63 | 57.96 | 11.1 | 7.8 | 23.5421 | YES | 300
15 | 1.13 | 63 | 71.19 | 11.5 | 7.8 | 23.479 | YES | 300
16 | 1.113 | 63 | 70.119 | 11.6 | 7.8 | 23.2786 | YES | 300
17 | 0.87 | 63 | 54.81 | 11 | 7.8 | 23.5646 | YES | 300
18 | 0.9 | 63 | 56.7 | 11.4 | 7.7 | 22.228 | YES | 300
19 | 0.89 | 63 | 56.07 | 11.5 | 7.7 | 22.0568 | YES | 300
20 | 1.19 | 63 | 74.97 | 11.6 | 7.9 | 24.3307 | YES | 300
21 | 0.89 | 63 | 56.07 | 11.9 | 7.7 | 21.4831 | YES | 300
22 | 1.26 | 63 | 79.38 | 11.9 | 7.9 | 24.0405 | YES | 300
23 | 1.11 | 63 | 69.93 | 12.5 | 7.8 | 21.8896 | YES | 300
24 | 1.25 | 63 | 78.75 | 12 | 7.8 | 23.0246 | YES | 300
25 | 1.06 | 63 | 66.78 | 12 | 7.6 | 21.0059 | YES | 300
26 | 1.03 | 63 | 64.89 | 12.2 | 7.6 | 20.6625 | YES | 300
27 | 1.06 | 63 | 66.78 | 12.5 | 7.8 | 21.7662 | YES | 300
28 | 1.03 | 63 | 64.89 | 13.2 | 7.6 | 19.2385 | YES | 300
29 | 0.97 | 63 | 61.11 | 12.9 | 7.7 | 20.2239 | YES | 300
30 | 1.01 | 63 | 63.63 | 12.7 | 7.8 | 21.3587 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2