## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-05-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | NIS | 0.039 | 0.043 | 0.043 | NIS | 0.04
2 | NIS | NIS | 0.043 | 0.04 | 0.037 | NIS | 0.04
3 | 0.037 | 0.037 | 0.037 | 0.039 | NIS | NIS | 0.04
4 | NIS | NIS | 0.037 | 0.037 | 0.06 | NIS | 0.06
5 | NIS | NIS | 0.037 | 0.035 | 0.035 | NIS | 0.04
6 | NIS | NIS | 0.035 | NIS | NIS | 0.04 | 0.04
7 | NIS | NIS | 0.035 | NIS | NIS | NIS | 0.04
8 | NIS | NIS | 0.032 | 0.037 | 0.03 | NIS | 0.04
9 | NIS | NIS | 0.03 | 0.031 | 0.032 | NIS | 0.03
10 | 0.041 | 0.035 | 0.035 | 0.041 | NIS | NIS | 0.04
11 | NIS | NIS | 0.032 | 0.032 | 0.035 | NIS | 0.04
12 | NIS | NIS | 0.035 | 0.034 | 0.037 | NIS | 0.04
13 | 0.039 | 0.037 | 0.047 | 0.039 | NIS | NIS | 0.05
14 | NIS | NIS | 0.041 | 0.041 | 0.041 | NIS | 0.04
15 | 0.045 | 0.041 | 0.045 | 0.051 | 0.049 | NIS | 0.05
16 | NIS | NIS | 0.045 | 0.046 | 0.043 | NIS | 0.05
17 | NIS | NIS | 0.041 | 0.049 | 0.053 | NIS | 0.05
18 | 0.051 | 0.049 | 0.049 | NIS | 0.06 | NIS | 0.06
19 | 0.051 | 0.047 | 0.043 | NIS | 0.059 | 0.041 | 0.06
20 | 0.041 | 0.068 | NIS | NIS | NIS | 0.045 | 0.07
21 | 0.035 | 0.045 | NIS | NIS | NIS | 0.05 | 0.05
22 | 0.045 | 0.047 | 0.045 | NIS | NIS | NIS | 0.05
23 | NIS | NIS | 0.03 | 0.032 | 0.03 | 0.032 | 0.03
24 | 0.03 | 0.042 | 0.03 | 0.032 | 0.041 | 0.032 | 0.04
25 | 0.032 | 0.05 | 0.028 | NIS | 0.04 | NIS | 0.05
26 | 0.037 | 0.028 | 0.026 | NIS | NIS | 0.037 | 0.04
27 | 0.03 | 0.03 | 0.037 | 0.035 | 0.032 | 0.035 | 0.04
28 | NIS | NIS | 0.03 | 0.032 | 0.039 | 0.039 | 0.04
29 | NIS | NIS | 0.037 | 0.047 | 0.043 | 0.0449 | 0.05
30 | 0.043 | 0.039 | 0.039 | 0.035 | 0.03 | 0.039 | 0.04
31 | 0.039 | 0.037 | NIS | NIS | NIS | NIS | 0.04
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | DATE:6/6/2023
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2023-06-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.96 | 63 | 60.48 | 13.2 | 7.7 | 19.8031 | YES | 300
2 | 1.06 | 63 | 66.78 | 13.3 | 7.9 | 21.4164 | YES | 300
3 | 1.01 | 63 | 63.63 | 13.2 | 7.9 | 21.4372 | YES | 300
4 | 0.93 | 63 | 58.59 | 13.6 | 7.7 | 19.2189 | YES | 300
5 | 0.97 | 63 | 61.11 | 13.6 | 7.8 | 20.0309 | YES | 300
6 | 0.88 | 63 | 55.44 | 13 | 7.8 | 20.6325 | YES | 300
7 | 1.1 | 63 | 69.3 | 13.1 | 7.7 | 20.2535 | YES | 300
8 | 0.83 | 63 | 52.29 | 14.2 | 7.9 | 19.6575 | YES | 300
9 | 1.05 | 63 | 66.15 | 14.4 | 7.7 | 18.4742 | YES | 300
10 | 1.12 | 63 | 70.56 | 15 | 7.8 | 18.5664 | YES | 300
11 | 0.88 | 63 | 55.44 | 15.3 | 7.7 | 17.0684 | YES | 300
12 | 1.01 | 63 | 63.63 | 15.4 | 7.8 | 17.855 | YES | 300
13 | 1.12 | 63 | 70.56 | 16 | 8 | 18.7035 | YES | 300
14 | 1.01 | 63 | 63.63 | 16.9 | 8 | 17.3988 | YES | 300
15 | 1.01 | 63 | 63.63 | 16.9 | 8.1 | 18.0534 | YES | 300
16 | 0.99 | 63 | 62.37 | 17.3 | 8.1 | 17.5397 | YES | 300
17 | 0.87 | 63 | 54.81 | 17.8 | 8.1 | 16.7358 | YES | 300
18 | 0.7 | 63 | 44.1 | 18 | 8.2 | 16.8085 | YES | 300
19 | 0.99 | 63 | 62.37 | 18.6 | 8 | 15.5006 | YES | 300
20 | 0.93 | 63 | 58.59 | 18.6 | 8.2 | 16.5782 | YES | 300
21 | 0.9 | 63 | 56.7 | 18.7 | 8.2 | 16.412 | YES | 300
22 | 0.91 | 63 | 57.33 | 18.6 | 8.2 | 16.5405 | YES | 300
23 | 0.8 | 63 | 50.4 | 18.6 | 7.9 | 14.6163 | YES | 300
24 | 0.89 | 63 | 56.07 | 18.9 | 8 | 15.0211 | YES | 300
25 | 0.99 | 63 | 62.37 | 19.1 | 8 | 14.9919 | YES | 300
26 | 1.02 | 63 | 64.26 | 19.5 | 8.1 | 15.2001 | YES | 300
27 | 1 | 63 | 63 | 20.2 | 8.2 | 15.0198 | YES | 300
28 | 0.93 | 63 | 58.59 | 19.9 | 8.2 | 15.2018 | YES | 300
29 | 0.94 | 63 | 59.22 | 20.5 | 8.3 | 15.1739 | YES | 300
30 | 0.93 | 63 | 58.59 | 20 | 8.2 | 15.1007 | YES | 300
31 | 0.97 | 63 | 61.11 | 20.2 | 8.3 | 15.5337 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2