## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-06-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.039 | 0.053 | NIS | NIS | 0.076 | 0.034 | 0.08
2 | 0.049 | 0.039 | NIS | NIS | 0.051 | NIS | 0.05
3 | NIS | NIS | 0.05 | NIS | 0.052 | NIS | 0.05
4 | NIS | NIS | 0.032 | NIS | 0.045 | NIS | 0.05
5 | NIS | NIS | 0.03 | NIS | NIS | NIS | 0.03
6 | 0.032 | 0.028 | 0.028 | NIS | 0.055 | NIS | 0.06
7 | NIS | NIS | 0.057 | 0.03 | 0.028 | NIS | 0.06
8 | 0.032 | 0.03 | NIS | NIS | 0.041 | 0.03 | 0.04
9 | 0.026 | 0.028 | NIS | NIS | NIS | 0.028 | 0.03
10 | NIS | NIS | 0.026 | NIS | 0.053 | NIS | 0.05
11 | 0.035 | 0.037 | 0.037 | NIS | NIS | 0.045 | 0.05
12 | 0.039 | 0.035 | NIS | NIS | 0.072 | 0.049 | 0.07
13 | 0.074 | 0.095 | 0.12 | NIS | 0.064 | 0.068 | 0.12
14 | 0.057 | 0.037 | 0.039 | NIS | NIS | 0.047 | 0.06
15 | 0.039 | 0.037 | 0.03 | NIS | NIS | 0.035 | 0.04
16 | 0.034 | 0.032 | 0.041 | 0.04 | NIS | 0.03 | 0.04
17 | 0.041 | 0.041 | 0.03 | NIS | NIS | 0.07 | 0.07
18 | 0.03 | NIS | 0.05 | NIS | NIS | 0.03 | 0.05
19 | 0.028 | 0.032 | 0.03 | NIS | NIS | NIS | 0.03
20 | 0.028 | 0.028 | NIS | NIS | NIS | 0.03 | 0.03
21 | 0.03 | 0.028 | 0.03 | NIS | NIS | 0.03 | 0.03
22 | 0.032 | 0.035 | 0.026 | NIS | NIS | 0.03 | 0.04
23 | 0.035 | 0.032 | 0.026 | NIS | NIS | NIS | 0.04
24 | NIS | 0.041 | 0.035 | 0.03 | 0.05 | NIS | 0.05
25 | 0.037 | 0.041 | 0.047 | 0.028 | 0.058 | NIS | 0.06
26 | 0.035 | 0.043 | 0.032 | NIS | 0.043 | 0.035 | 0.04
27 | NIS | NIS | 0.037 | 0.034 | NIS | NIS | 0.04
28 | 0.053 | 0.053 | 0.032 | 0.07 | 0.043 | 0.04 | 0.07
29 | 0.041 | 0.041 | 0.066 | NIS | NIS | NIS | 0.07
30 | 0.035 | 0.035 | 0.043 | 0.041 | NIS | NIS | 0.04
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | DATE: 7/5/2023
[5 empty] | PHONE #: ( 541 419-7958 |  |  | CERT #: 6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2023-06-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.97 | 63 | 61.11 | 20.2 | 8 | 13.8974 | YES | 300
2 | 1 | 63 | 63 | 20.1 | 8 | 14.0387 | YES | 300
3 | 0.96 | 63 | 60.48 | 19.7 | 8 | 14.3536 | YES | 300
4 | 0.97 | 63 | 61.11 | 20.3 | 8.4 | 16.0126 | YES | 300
5 | 1.03 | 63 | 64.89 | 20.5 | 8.4 | 15.9089 | YES | 300
6 | 0.96 | 63 | 60.48 | 20.8 | 8.3 | 14.9069 | YES | 300
7 | 0.88 | 63 | 55.44 | 21.1 | 7.6 | 11.1543 | YES | 300
8 | 0.94 | 63 | 59.22 | 21.3 | 7.4 | 10.2809 | YES | 300
9 | 1.02 | 63 | 64.26 | 21.4 | 7.3 | 9.9265 | YES | 300
10 | 0.74 | 63 | 46.62 | 21.6 | 7.2 | 9.1302 | YES | 300
11 | 0.73 | 63 | 45.99 | 21.6 | 7.6 | 10.5997 | YES | 300
12 | 0.83 | 63 | 52.29 | 21.8 | 7.6 | 10.5788 | YES | 300
13 | 0.73 | 63 | 45.99 | 22.1 | 8.1 | 12.3556 | YES | 300
14 | 0.91 | 63 | 57.33 | 22.2 | 8 | 12.0701 | YES | 300
15 | 0.93 | 63 | 58.59 | 21.7 | 7.9 | 12.0529 | YES | 300
16 | 0.8 | 63 | 50.4 | 21.7 | 7.9 | 11.8744 | YES | 300
17 | 0.96 | 63 | 60.48 | 22.1 | 8 | 12.2214 | YES | 300
18 | 0.93 | 63 | 58.59 | 21.9 | 7.8 | 11.4559 | YES | 300
19 | 0.74 | 63 | 46.62 | 21.2 | 7.8 | 11.749 | YES | 300
20 | 1.05 | 63 | 66.15 | 20.7 | 7.9 | 13.0681 | YES | 300
21 | 0.89 | 63 | 56.07 | 20.4 | 7.7 | 12.1512 | YES | 300
22 | 0.92 | 63 | 57.96 | 20.8 | 7.6 | 11.4344 | YES | 300
23 | 0.99 | 63 | 62.37 | 21.1 | 7.5 | 10.8813 | YES | 300
24 | 0.95 | 63 | 59.85 | 21.4 | 7.6 | 11.0194 | YES | 300
25 | 0.93 | 63 | 58.59 | 21.7 | 7.6 | 10.7739 | YES | 300
26 | 1 | 63 | 63 | 21.9 | 7.8 | 11.5484 | YES | 300
27 | 1 | 63 | 63 | 22.1 | 7.8 | 11.394 | YES | 300
28 | 0.96 | 63 | 60.48 | 22.6 | 7.9 | 11.3841 | YES | 300
29 | 0.93 | 63 | 58.59 | 23 | 7.7 | 10.2456 | YES | 300
30 | 0.71 | 63 | 44.73 | 23.4 | 7.7 | 9.7217 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2