## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-07-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | NIS | 0.041 | NIS | NIS | NIS | 0.04
2 | NIS | NIS | 0.067 | 0.062 | NIS | 0.055 | 0.07
3 | NIS | NIS | 0.043 | NIS | 0.049 | NIS | 0.05
4 | NIS | NIS | 0.055 | NIS | NIS | 0.055 | 0.06
5 | 0.045 | 0.045 | 0.045 | NIS | NIS | NIS | 0.05
6 | 0.051 | 0.051 | 0.053 | 0.055 | NIS | NIS | 0.06
7 | 0.066 | 0.049 | 0.049 | 0.054 | NIS | NIS | 0.07
8 | 0.051 | 0.049 | 0.043 | 0.049 | 0.066 | NIS | 0.07
9 | NIS | NIS | 0.041 | 0.045 | NIS | NIS | 0.05
10 | 0.055 | 0.045 | 0.045 | NIS | NIS | 0.06 | 0.06
11 | 0.053 | 0.047 | 0.053 | NIS | NIS | NIS | 0.05
12 | 0.057 | 0.055 | 0.051 | 0.053 | NIS | NIS | 0.06
13 | 0.053 | 0.062 | 0.053 | NIS | NIS | 0.074 | 0.07
14 | 0.062 | 0.07 | NIS | 0.055 | NIS | 0.055 | 0.07
15 | 0.037 | 0.045 | 0.06 | 0.04 | NIS | 0.04 | 0.06
16 | 0.049 | 0.045 | NIS | NIS | NIS | 0.03 | 0.05
17 | 0.051 | 0.043 | 0.053 | NIS | NIS | NIS | 0.05
18 | 0.03 | 0.045 | 0.039 | NIS | NIS | 0.06 | 0.06
19 | 0.055 | 0.049 | 0.041 | NIS | NIS | 0.051 | 0.06
20 | 0.049 | 0.049 | 0.047 | 0.051 | NIS | NIS | 0.05
21 | 0.053 | 0.047 | 0.047 | 0.054 | NIS | NIS | 0.05
22 | NIS | NIS | 0.049 | NIS | 0.085 | 0.077 | 0.09
23 | 0.057 | 0.057 | 0.045 | NIS | NIS | NIS | 0.06
24 | 0.062 | 0.047 | 0.053 | NIS | NIS | NIS | 0.06
25 | 0.066 | 0.057 | 0.052 | 0.062 | NIS | NIS | 0.07
26 | NIS | NIS | 0.06 | 0.06 | NIS | NIS | 0.06
27 | 0.059 | 0.066 | 0.05 | NIS | NIS | NIS | 0.07
28 | NIS | NIS | 0.049 | 0.069 | NIS | NIS | 0.07
29 | NIS | NIS | 0.054 | NIS | NIS | NIS | 0.05
30 | NIS | NIS | 0.059 | NIS | 0.067 | 0.064 | 0.07
31 | 0.057 | NIS | 0.043 | 0.048 | NIS | NIS | 0.06
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony Rogers
[5 empty] | SIGNATURE: |  |  | DATE: 8/3/2023
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2023-07-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.86 | 63 | 54.18 | 23.6 | 7.7 | 9.7588 | YES | 300
2 | 0.94 | 63 | 59.22 | 23.9 | 7.7 | 9.6514 | YES | 300
3 | 0.87 | 63 | 54.81 | 23.7 | 8 | 10.8608 | YES | 300
4 | 0.92 | 63 | 57.96 | 23.8 | 8 | 10.8501 | YES | 300
5 | 1.02 | 63 | 64.26 | 24.3 | 7.7 | 9.4806 | YES | 300
6 | 0.98 | 63 | 61.74 | 24.6 | 8 | 10.351 | YES | 300
7 | 0.89 | 63 | 56.07 | 24.6 | 8.1 | 10.6356 | YES | 300
8 | 0.9 | 63 | 56.7 | 24.3 | 8.1 | 10.8656 | YES | 300
9 | 0.9 | 63 | 56.7 | 24 | 8.1 | 11.0876 | YES | 300
10 | 0.92 | 63 | 57.96 | 24.2 | 8.1 | 10.9644 | YES | 300
11 | 0.98 | 63 | 61.74 | 24.2 | 8.1 | 11.0404 | YES | 300
12 | 0.98 | 63 | 61.74 | 24.2 | 8.1 | 11.0404 | YES | 300
13 | 1.02 | 63 | 64.26 | 24.8 | 8.2 | 11.058 | YES | 300
14 | 0.83 | 63 | 52.29 | 25.1 | 8.2 | 10.6019 | YES | 300
15 | 0.94 | 63 | 59.22 | 25.5 | 8.3 | 10.8503 | YES | 300
16 | 1.06 | 63 | 66.78 | 25.8 | 8.4 | 11.1922 | YES | 300
17 | 0.93 | 63 | 58.59 | 25.7 | 8.3 | 10.6926 | YES | 300
18 | 0.91 | 63 | 57.33 | 25.5 | 8.4 | 11.2254 | YES | 300
19 | 0.93 | 63 | 58.59 | 25.4 | 8.5 | 11.7586 | YES | 300
20 | 0.93 | 63 | 58.59 | 25.8 | 8.5 | 11.4464 | YES | 300
21 | 1 | 63 | 63 | 25.4 | 8.4 | 11.4188 | YES | 300
22 | 0.9 | 63 | 56.7 | 25.2 | 8.5 | 11.8768 | YES | 300
23 | 0.9 | 63 | 56.7 | 25.7 | 8.5 | 11.484 | YES | 300
24 | 0.7 | 63 | 44.1 | 25.6 | 8.6 | 11.7291 | YES | 300
25 | 0.92 | 63 | 57.96 | 26 | 8.5 | 11.2803 | YES | 300
26 | 0.95 | 63 | 59.85 | 25.5 | 8.5 | 11.7067 | YES | 300
27 | 0.93 | 63 | 58.59 | 25 | 8.5 | 12.0791 | YES | 300
28 | 0.87 | 63 | 54.81 | 25 | 8.6 | 12.4522 | YES | 300
29 | 0.93 | 63 | 58.59 | 25.2 | 8.7 | 12.8407 | YES | 300
30 | 0.71 | 63 | 44.73 | 25.1 | 8.7 | 12.6054 | YES | 300
31 | 0.82 | 63 | 51.66 | 24.8 | 8.6 | 12.5484 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2