## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-08-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | NIS | 0.041 | 0.07 | 0.05 | 0.06 | 0.07
2 | 0.05 | NIS | NIS | NIS | NIS | 0.06 | 0.06
3 | NIS | NIS | 0.064 | 0.066 | 0.067 | 0.073 | 0.07
4 | NIS | NIS | 0.066 | 0.062 | 0.065 | 0.073 | 0.07
5 | 0.039 | 0.057 | NIS | NIS | NIS | NIS | 0.06
6 | NIS | 0.055 | 0.062 | 0.066 | 0.08 | NIS | 0.08
7 | NIS | 0.06 | 0.07 | 0.066 | 0.082 | NIS | 0.08
8 | 0.07 | 0.07 | 0.07 | 0.07 | NIS | NIS | 0.07
9 | NIS | 0.062 | 0.06 | 0.07 | NIS | NIS | 0.07
10 | NIS | NIS | 0.039 | 0.037 | NIS | 0.053 | 0.05
11 | 0.05 | 0.041 | 0.04 | NIS | NIS | NIS | 0.05
12 | NIS | NIS | 0.06 | NIS | NIS | 0.057 | 0.06
13 | 0.049 | 0.036 | 0.045 | NIS | 0.05 | 0.07 | 0.07
14 | 0.05 | NIS | NIS | NIS | NIS | NIS | 0.05
15 | NIS | NIS | NIS | 0.06 | 0.05 | 0.052 | 0.06
16 | 0.05 | 0.07 | 0.05 | 0.07 | 0.07 | 0.06 | 0.07
17 | NIS | NIS | 0.05 | 0.059 | NIS | NIS | 0.06
18 | NIS | NIS | 0.055 | 0.045 | 0.06 | NIS | 0.06
19 | NIS | NIS | 0.045 | 0.08 | NIS | NIS | 0.08
20 | NIS | NIS | NIS | NIS | NIS | 0.085 | 0.09
21 | 0.064 | 0.051 | 0.052 | 0.051 | 0.057 | NIS | 0.06
22 | NIS | NIS | 0.042 | NIS | NIS | NIS | 0.04
23 | NIS | NIS | 0.051 | 0.047 | NIS | NIS | 0.05
24 | NIS | NIS | 0.043 | 0.049 | NIS | NIS | 0.05
25 | NIS | NIS | 0.055 | 0.05 | NIS | NIS | 0.06
26 | NIS | NIS | 0.048 | 0.047 | 0.065 | 0.051 | 0.07
27 | 0.053 | 0.047 | 0.048 | NIS | NIS | NIS | 0.05
28 | NIS | NIS | 0.055 | 0.045 | 0.05 | 0.08 | 0.08
29 | NIS | NIS | 0.066 | NIS | NIS | NIS | 0.07
30 | NIS | NIS | 0.049 | 0.052 | 0.057 | NIS | 0.06
31 | 0.062 | 0.072 | 0.049 | NIS | NIS | NIS | 0.07
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | DATE: 9/1/2023
[5 empty] | PHONE #: ( 541 ) 419-7958 |  |  | CERT #: 6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2023-08-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.65 | 63 | 40.95 | 24.7 | 8.5 | 11.9353 | YES | 300
2 | 0.9 | 63 | 56.7 | 24.7 | 8.5 | 12.2827 | YES | 300
3 | 0.97 | 63 | 61.11 | 24.5 | 8.6 | 13.0253 | YES | 300
4 | 1.01 | 63 | 63.63 | 24.7 | 8.5 | 12.4386 | YES | 300
5 | 1.4 | 63 | 88.2 | 24.5 | 8.8 | 14.737 | YES | 300
6 | 0.92 | 63 | 57.96 | 25.3 | 8.7 | 12.7402 | YES | 300
7 | 1.05 | 63 | 66.15 | 25.4 | 8.8 | 13.3321 | YES | 300
8 | 1.17 | 63 | 73.71 | 25.6 | 8.7 | 12.8492 | YES | 300
9 | 1.2 | 63 | 75.6 | 25.4 | 8.9 | 14.0763 | YES | 300
10 | 1.21 | 63 | 76.23 | 25.7 | 8.9 | 13.8124 | YES | 300
11 | 1.15 | 63 | 72.45 | 25.5 | 8.9 | 13.9028 | YES | 300
12 | 1.03 | 63 | 64.89 | 25 | 8.7 | 13.1638 | YES | 300
13 | 0.88 | 63 | 55.44 | 25.4 | 8.8 | 13.0752 | YES | 300
14 | 1.18 | 63 | 74.34 | 25.6 | 8.7 | 12.8639 | YES | 300
15 | 1.08 | 63 | 68.04 | 25.5 | 8.7 | 12.803 | YES | 300
16 | 1.09 | 63 | 68.67 | 26.3 | 8.8 | 12.609 | YES | 300
17 | 0.95 | 63 | 59.85 | 26.5 | 8.6 | 11.3616 | YES | 300
18 | 0.75 | 63 | 47.25 | 26.1 | 8.6 | 11.4064 | YES | 300
19 | 1.19 | 63 | 74.97 | 26 | 8.7 | 12.5376 | YES | 300
20 | 0.81 | 63 | 51.03 | 26.5 | 8.8 | 12.0477 | YES | 300
21 | 1.1 | 63 | 69.3 | 24.5 | 8.8 | 14.2409 | YES | 300
22 | 0.98 | 63 | 61.74 | 24.3 | 8.9 | 14.7746 | YES | 300
23 | 1.03 | 63 | 64.89 | 23.6 | 8.8 | 15.0033 | YES | 300
24 | 0.99 | 63 | 62.37 | 23.5 | 8.9 | 15.6027 | YES | 300
25 | 0.9 | 63 | 56.7 | 23.3 | 8.8 | 15.0816 | YES | 300
26 | 1.1 | 63 | 69.3 | 23.6 | 9 | 16.2863 | YES | 300
27 | 1.13 | 63 | 71.19 | 23.8 | 9 | 16.1257 | YES | 300
28 | 0.73 | 63 | 45.99 | 23.6 | 8.8 | 14.4985 | YES | 300
29 | 1.45 | 63 | 91.35 | 23.4 | 8.9 | 16.5513 | YES | 300
30 | 1.05 | 63 | 66.15 | 23 | 8.8 | 15.6518 | YES | 300
31 | 1.04 | 63 | 65.52 | 23.1 | 8.8 | 15.53 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2