## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-09-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | NIS | 0.066 | 0.051 | NIS | NIS | 0.07
2 | NIS | NIS | 0.068 | 0.066 | NIS | NIS | 0.07
3 | NIS | NIS | 0.06 | NIS | NIS | NIS | 0.06
4 | NIS | 0.049 | 0.052 | 0.049 | 0.06 | 0.05 | 0.06
5 | 0.05 | NIS | 0.04 | NIS | NIS | NIS | 0.05
6 | NIS | NIS | NIS | 0.053 | 0.06 | 0.053 | 0.06
7 | 0.053 | 0.051 | 0.06 | NIS | NIS | NIS | 0.06
8 | NIS | NIS | 0.059 | NIS | NIS | 0.08 | 0.08
9 | 0.059 | 0.08 | 0.09 | NIS | NIS | 0.1 | 0.1
10 | 0.064 | 0.1 | 0.066 | NIS | NIS | NIS | 0.1
11 | NIS | NIS | 0.062 | 0.06 | NIS | NIS | 0.06
12 | 0.091 | 0.093 | 0.074 | NIS | NIS | NIS | 0.09
13 | 0.078 | 0.07 | NIS | 0.065 | NIS | NIS | 0.08
14 | NIS | 0.066 | 0.078 | 0.068 | NIS | NIS | 0.08
15 | NIS | NIS | 0.066 | 0.068 | 0.08 | NIS | 0.08
16 | NIS | NIS | 0.067 | 0.076 | NIS | NIS | 0.08
17 | NIS | NIS | 0.065 | 0.07 | NIS | NIS | 0.07
18 | NIS | 0.07 | 0.066 | 0.068 | 0.06 | NIS | 0.07
19 | NIS | 0.068 | 0.07 | 0.07 | NIS | 0.07 | 0.07
20 | 0.07 | 0.07 | 0.082 | NIS | NIS | NIS | 0.08
21 | NIS | NIS | 0.064 | 0.074 | NIS | NIS | 0.07
22 | 0.074 | 0.082 | 0.074 | NIS | NIS | NIS | 0.08
23 | NIS | NIS | 0.069 | 0.08 | NIS | NIS | 0.08
24 | NIS | NIS | 0.059 | 0.062 | NIS | NIS | 0.06
25 | 0.08 | 0.07 | 0.066 | NIS | NIS | 0.092 | 0.092
26 | 0.072 | 0.061 | NIS | NIS | NIS | NIS | 0.07
27 | NIS | NIS | 0.068 | 0.072 | NIS | NIS | 0.07
28 | 0.068 | 0.064 | 0.068 | NIS | NIS | NIS | 0.07
29 | NIS | NIS | 0.074 | 0.06 | NIS | NIS | 0.07
30 | NIS | NIS | 0.055 | 0.056 | 0.069 | NIS | 0.07
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | DATE:10/4/2023
[5 empty] | PHONE #: ( 541 ) 459-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2023-09-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.82 | 63 | 51.66 | 22.8 | 8.7 | 14.8895 | YES | 300
2 | 1.29 | 63 | 81.27 | 22.9 | 8.9 | 16.8032 | YES | 300
3 | 1.02 | 63 | 64.26 | 22.4 | 8.5 | 14.5267 | YES | 300
4 | 1.1 | 63 | 69.3 | 22.7 | 8.7 | 15.4753 | YES | 300
5 | 0.9 | 63 | 56.7 | 22 | 8.8 | 16.4474 | YES | 300
6 | 1.11 | 63 | 69.93 | 22.3 | 8.8 | 16.5117 | YES | 300
7 | 1.12 | 63 | 70.56 | 22 | 9 | 18.1572 | YES | 300
8 | 0.75 | 63 | 47.25 | 21.9 | 8.8 | 16.2771 | YES | 300
9 | 1.1 | 63 | 69.3 | 22 | 8.9 | 17.4592 | YES | 300
10 | 1.06 | 63 | 66.78 | 21.9 | 9 | 18.1542 | YES | 300
11 | 1.05 | 63 | 66.15 | 21.7 | 9 | 18.3763 | YES | 300
12 | 0.88 | 63 | 55.44 | 21.5 | 9 | 18.2663 | YES | 300
13 | 1.01 | 63 | 63.63 | 22.1 | 9.1 | 18.4829 | YES | 300
14 | 0.92 | 63 | 57.96 | 21.8 | 9.1 | 18.6634 | YES | 300
15 | 0.99 | 63 | 62.37 | 21.7 | 8.9 | 17.59 | YES | 300
16 | 1.08 | 63 | 68.04 | 21.9 | 9.2 | 19.5884 | YES | 300
17 | 1.13 | 63 | 71.19 | 22 | 9.4 | 21.0651 | YES | 300
18 | 1.1 | 63 | 69.3 | 21.7 | 9.2 | 19.895 | YES | 300
19 | 1.12 | 63 | 70.56 | 20.8 | 9.2 | 21.166 | YES | 300
20 | 1.12 | 63 | 70.56 | 20.7 | 9.2 | 21.3067 | YES | 300
21 | 1.26 | 63 | 79.38 | 19.9 | 9.2 | 22.824 | YES | 300
22 | 1.1 | 63 | 69.3 | 19.6 | 9.3 | 23.7199 | YES | 300
23 | 0.87 | 63 | 54.81 | 19.6 | 9.3 | 23.1118 | YES | 300
24 | 1.05 | 63 | 66.15 | 19.7 | 9.2 | 22.5857 | YES | 300
25 | 1.04 | 63 | 65.52 | 19.6 | 9.2 | 22.71 | YES | 300
26 | 1.28 | 63 | 80.64 | 19 | 9.1 | 23.4031 | YES | 300
27 | 1.13 | 63 | 71.19 | 19.2 | 9.3 | 24.4381 | YES | 300
28 | 1.14 | 63 | 71.82 | 18.4 | 9.2 | 24.8644 | YES | 300
29 | 1.14 | 63 | 71.82 | 18.6 | 9.1 | 23.6534 | YES | 300
30 | 1.23 | 63 | 77.49 | 18.9 | 9.1 | 23.4257 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2