## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-10-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | NIS | 0.06 | 0.08 | NIS | NIS | 0.08
2 | NIS | NIS | 0.06 | 0.06 | NIS | NIS | 0.06
3 | NIS | NIS | 0.06 | 0.06 | NIS | NIS | 0.06
4 | NIS | NIS | 0.07 | 0.07 | 0.07 | 0.08 | 0.08
5 | 0.08 | 0.08 | 0.07 | NIS | NIS | NIS | 0.08
6 | NIS | NIS | 0.08 | 0.08 | NIS | NIS | 0.08
7 | NIS | 0.09 | 0.06 | NIS | NIS | NIS | 0.09
8 | NIS | 0.09 | 0.06 | NIS | NIS | NIS | 0.09
9 | 0.08 | 0.09 | 0.08 | NIS | NIS | NIS | 0.09
10 | 0.08 | 0.09 | 0.09 | NIS | NIS | NIS | 0.09
11 | NIS | NIS | 0.08 | 0.1 | 0.1 | NIS | 0.1
12 | NIS | NIS | 0.09 | 0.1 | NIS | NIS | 0.1
13 | NIS | NIS | 0.1 | 0.17 | 0.09 | NIS | 0.17
14 | NIS | NIS | 0.08 | 0.09 | 0.09 | NIS | 0.09
15 | NIS | NIS | 0.08 | 0.08 | 0.09 | 0.1 | 0.1
16 | NIS | NIS | 0.08 | 0.08 | NIS | NIS | 0.08
17 | NIS | NIS | 0.08 | 0.08 | 0.09 | NIS | 0.09
18 | NIS | 0.11 | 0.13 | NIS | NIS | 0.08 | 0.13
19 | 0.08 | 0.08 | 0.08 | NIS | NIS | NIS | 0.08
20 | NIS | NIS | 0.08 | 0.07 | NIS | NIS | 0.08
21 | NIS | NIS | 0.07 | 0.07 | 0.07 | NIS | 0.07
22 | 0.08 | NIS | NIS | NIS | 0.1 | 0.08 | 0.1
23 | NIS | NIS | 0.07 | 0.08 | 0.1 | NIS | 0.1
24 | NIS | NIS | 0.1 | NIS | NIS | NIS | 0.1
25 | NIS | NIS | 0.08 | 0.07 | NIS | NIS | 0.08
26 | NIS | NIS | 0.06 | 0.07 | NIS | NIS | 0.07
27 | NIS | NIS | 0.06 | 0.06 | NIS | NIS | 0.06
28 | NIS | NIS | 0.06 | 0.06 | NIS | NIS | 0.06
29 | NIS | NIS | 0.06 | 0.06 | NIS | NIS | 0.06
30 | NIS | NIS | 0.04 | 0.04 | 0.05 | NIS | 0.05
31 | NIS | NIS | 0.04 | 0.04 | 0.05 | NIS | 0.05
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | 2023-11-06
[5 empty] | PHONE #: ( 541 ) 459-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2023-10-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.97 | 63 | 61.11 | 17.8 | 9.1 | 24.464 | YES | 300
2 | 1.26 | 63 | 79.38 | 17.1 | 9.2 | 27.4615 | YES | 300
3 | 1.18 | 63 | 74.34 | 17.8 | 9.2 | 25.9864 | YES | 300
4 | 1.12 | 63 | 70.56 | 17.8 | 9.1 | 24.8815 | YES | 300
5 | 1.12 | 63 | 70.56 | 18.3 | 9.1 | 24.0728 | YES | 300
6 | 1.18 | 63 | 74.34 | 18.1 | 9 | 23.6737 | YES | 300
7 | 1.06 | 63 | 66.78 | 18.2 | 9.1 | 24.0689 | YES | 300
8 | 1.15 | 63 | 72.45 | 18.4 | 9.2 | 24.8924 | YES | 300
9 | 1.16 | 63 | 73.08 | 18.5 | 9.1 | 23.8642 | YES | 300
10 | 1.19 | 63 | 74.97 | 18.3 | 9.2 | 25.1707 | YES | 300
11 | 1.09 | 63 | 68.67 | 17.7 | 9 | 24.0623 | YES | 300
12 | 1.16 | 63 | 73.08 | 17.7 | 9.1 | 25.1597 | YES | 300
13 | 1.16 | 63 | 73.08 | 17.5 | 9 | 24.5759 | YES | 300
14 | 1.16 | 63 | 73.08 | 17.4 | 9 | 24.7388 | YES | 300
15 | 1.25 | 63 | 78.75 | 17.5 | 9.1 | 25.7543 | YES | 300
16 | 1.18 | 63 | 74.34 | 17.4 | 8.9 | 23.9011 | YES | 300
17 | 0.85 | 63 | 53.55 | 17.4 | 8.9 | 23.0268 | YES | 300
18 | 1.15 | 63 | 72.45 | 17.6 | 8.8 | 22.6594 | YES | 300
19 | 1.09 | 63 | 68.67 | 17.4 | 8.8 | 22.8061 | YES | 300
20 | 1.16 | 63 | 73.08 | 17.7 | 8.9 | 23.3788 | YES | 300
21 | 0.94 | 63 | 59.22 | 17.7 | 8.8 | 21.9819 | YES | 300
22 | 1.13 | 63 | 71.19 | 17.7 | 8.8 | 22.4591 | YES | 300
23 | 1.13 | 63 | 71.19 | 17.9 | 8.9 | 22.9935 | YES | 300
24 | 1.2 | 63 | 75.6 | 17.1 | 8.8 | 23.554 | YES | 300
25 | 1.16 | 63 | 73.08 | 16.4 | 8.8 | 24.5584 | YES | 300
26 | 1.28 | 63 | 80.64 | 15.8 | 8.8 | 25.8994 | YES | 300
27 | 1.22 | 63 | 76.86 | 15.2 | 8.7 | 25.8007 | YES | 300
28 | 1.29 | 63 | 81.27 | 15.2 | 8.7 | 26.0051 | YES | 300
29 | 1.19 | 63 | 74.97 | 14 | 8.7 | 27.8326 | YES | 300
30 | 1.2 | 63 | 75.6 | 13.8 | 8.6 | 27.2184 | YES | 300
31 | 1.31 | 63 | 82.53 | 13.7 | 8.6 | 27.7401 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2