## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-11-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | NIS | 0.051 | 0.037 | NIS | NIS | 0.051
2 | NIS | NIS | 0.035 | 0.043 | 0.039 | NIS | 0.04
3 | NIS | NIS | 0.032 | 0.048 | 0.04 | NIS | 0.05
4 | 0.04 | NIS | NIS | NIS | NIS | 0.028 | 0.04
5 | 0.08 | 0.04 | NIS | NIS | 0.05 | NIS | 0.08
6 | 0.03 | NIS | 0.03 | NIS | NIS | 0.04 | 0.04
7 | NIS | NIS | 0.076 | 0.032 | NIS | NIS | 0.08
8 | NIS | NIS | 0.032 | 0.028 | NIS | NIS | 0.03
9 | NIS | NIS | 0.037 | 0.032 | NIS | NIS | 0.04
10 | 0.032 | 0.03 | 0.032 | NIS | NIS | NIS | 0.03
11 | NIS | NIS | NIS | NIS | 0.097 | 0.067 | 0.1
12 | 0.032 | 0.032 | 0.065 | 0.032 | NIS | NIS | 0.07
13 | NIS | NIS | 0.032 | 0.03 | 0.03 | NIS | 0.03
14 | NIS | NIS | 0.035 | 0.028 | 0.05 | NIS | 0.05
15 | NIS | NIS | 0.045 | 0.032 | 0.028 | NIS | 0.05
16 | NIS | NIS | 0.078 | 0.028 | NIS | NIS | 0.08
17 | NIS | NIS | 0.045 | 0.039 | 0.054 | 0.03 | 0.05
18 | 0.03 | NIS | NIS | NIS | NIS | 0.031 | 0.03
19 | 0.03 | 0.03 | 0.03 | NIS | NIS | NIS | 0.03
20 | NIS | NIS | 0.062 | 0.05 | 0.049 | NIS | 0.06
21 | NIS | NIS | 0.054 | 0.032 | 0.026 | NIS | 0.05
22 | NIS | NIS | 0.026 | 0.058 | 0.051 | 0.03 | 0.06
23 | 0.03 | NIS | 0.035 | NIS | NIS | NIS | 0.04
24 | NIS | NIS | 0.062 | 0.02 | NIS | NIS | 0.06
25 | NIS | NIS | 0.06 | 0.03 | 0.07 | NIS | 0.07
26 | NIS | NIS | 0.03 | 0.08 | NIS | NIS | 0.08
27 | NIS | NIS | 0.079 | 0.06 | 0.046 | NIS | 0.08
28 | NIS | NIS | NIS | NIS | 0.054 | NIS | 0.05
29 | NIS | NIS | NIS | 0.068 | 0.093 | 0.09 | 0.09
30 | 0.13 | 0.07 | NIS | 0.052 | NIS | NIS | 0.13
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | DATE: 12/5/2023
[5 empty] | PHONE #: ( 541 ) 459-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2023-11-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.23 | 63 | 77.49 | 14.3 | 8.5 | 25.4728 | YES | 300
2 | 1.23 | 63 | 77.49 | 14 | 8.4 | 25.0467 | YES | 300
3 | 1.21 | 63 | 76.23 | 13.8 | 8.3 | 24.4103 | YES | 300
4 | 1.03 | 63 | 64.89 | 13.8 | 8.4 | 24.8136 | YES | 300
5 | 1.19 | 63 | 74.97 | 14.4 | 8.2 | 22.5636 | YES | 300
6 | 1.04 | 63 | 65.52 | 15.4 | 8.1 | 20.0119 | YES | 300
7 | 1.29 | 63 | 81.27 | 14 | 7.8 | 20.2264 | YES | 300
8 | 1.21 | 63 | 76.23 | 14.6 | 7.7 | 18.5643 | YES | 300
9 | 1.08 | 63 | 68.04 | 13.7 | 7.8 | 20.1479 | YES | 300
10 | 1.08 | 63 | 68.04 | 13.3 | 7.5 | 18.5239 | YES | 300
11 | 1.19 | 63 | 74.97 | 13.6 | 7.5 | 18.3864 | YES | 300
12 | 1.15 | 63 | 72.45 | 13.1 | 7.3 | 17.5749 | YES | 300
13 | 0.95 | 63 | 59.85 | 13.5 | 7.4 | 17.3586 | YES | 300
14 | 1.19 | 63 | 74.97 | 13 | 7.4 | 18.441 | YES | 300
15 | 0.92 | 63 | 57.96 | 13.3 | 7.4 | 17.5312 | YES | 300
16 | 1.06 | 63 | 66.78 | 13.5 | 7.3 | 16.9392 | YES | 300
17 | 1.04 | 63 | 65.52 | 13.5 | 7.7 | 19.5896 | YES | 300
18 | 0.94 | 63 | 59.22 | 13.3 | 7.6 | 18.9172 | YES | 300
19 | 1.14 | 63 | 71.82 | 13.8 | 7.7 | 19.4223 | YES | 300
20 | 1.13 | 63 | 71.19 | 12.9 | 7.4 | 18.438 | YES | 300
21 | 1.11 | 63 | 69.93 | 12.5 | 7.7 | 21.099 | YES | 300
22 | 1.06 | 63 | 66.78 | 13.6 | 7.5 | 18.1172 | YES | 300
23 | 1 | 63 | 63 | 12.7 | 7.6 | 19.82 | YES | 300
24 | 1.02 | 63 | 64.26 | 12.5 | 7.7 | 20.8853 | YES | 300
25 | 0.84 | 63 | 52.92 | 11.8 | 7.7 | 21.5034 | YES | 300
26 | 0.9 | 63 | 56.7 | 11.3 | 7.8 | 23.1789 | YES | 300
27 | 0.93 | 63 | 58.59 | 10.5 | 7.7 | 23.6742 | YES | 300
28 | 0.9 | 63 | 56.7 | 10.7 | 7.8 | 24.1218 | YES | 300
29 | 0.83 | 63 | 52.29 | 10.4 | 7.6 | 22.7443 | YES | 300
30 | 0.87 | 63 | 54.81 | 9.6 | 7.7 | 24.966 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2