## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-03-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | NIS | 0.02 | 0.04 | 0.06 | NIS | 0.06
2 | NIS | NIS | 0.032 | 0.03 | 0.04 | NIS | 0.04
3 | NIS | NIS | 0.03 | 0.04 | 0.04 | NIS | 0.04
4 | NIS | NIS | 0.02 | 0.03 | 0.03 | 0.03 | 0.03
5 | NIS | NIS | 0.04 | 0.031 | 0.03 | NIS | 0.04
6 | NIS | NIS | 0.02 | NIS | NIS | NIS | 0.02
7 | NIS | NIS | 0.02 | 0.04 | 0.02 | 0.03 | 0.04
8 | 0.04 | NIS | 0.02 | NIS | NIS | NIS | 0.04
9 | NIS | NIS | 0.02 | 0.03 | 0.03 | 0.03 | 0.03
10 | NIS | NIS | 0.03 | 0.02 | 0.03 | 0.07 | 0.07
11 | 0.03 | 0.04 | 0.02 | NIS | NIS | NIS | 0.04
12 | NIS | NIS | 0.02 | 0.04 | 0.06 | NIS | 0.06
13 | NIS | NIS | 0.03 | 0.05 | 0.02 | 0.03 | 0.05
14 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
15 | 0.04 | NIS | NIS | 0.03 | NIS | NIS | 0.04
16 | NIS | NIS | 0.02 | 0.03 | 0.02 | NIS | 0.03
17 | NIS | NIS | 0.03 | 0.05 | 0.04 | 0.02 | 0.05
18 | NIS | NIS | NIS | 0.04 | 0.03 | 0.03 | 0.04
19 | NIS | NIS | 0.02 | 0.04 | 0.04 | NIS | 0.04
20 | NIS | NIS | 0.04 | 0.02 | 0.03 | NIS | 0.04
21 | NIS | NIS | 0.03 | 0.04 | 0.04 | NIS | 0.04
22 | NIS | NIS | 0.03 | 0.03 | 0.03 | NIS | 0.03
23 | NIS | NIS | 0.03 | 0.03 | 0.04 | NIS | 0.04
24 | NIS | NIS | 0.03 | 0.03 | NIS | NIS | 0.03
25 | NIS | NIS | 0.03 | 0.03 | 0.05 | NIS | 0.05
26 | NIS | NIS | 0.04 | 0.04 | NIS | NIS | 0.04
27 | NIS | NIS | 0.03 | 0.03 | 0.03 | NIS | 0.03
28 | NIS | NIS | 0.03 | 0.03 | NIS | NIS | 0.03
29 | NIS | NIS | 0.05 | 0.03 | 0.03 | NIS | 0.05
30 | NIS | NIS | 0.03 | NIS | NIS | NIS | 0.03
31 | NIS | NIS | 0.03 | 0.03 | NIS | NIS | 0.03
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | DATE: 4/5/2024
[5 empty] | PHONE #: ( 541 ) 459-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2024-03-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.35 | 63 | 85.05 | 10.1 | 7.2 | 21.3749 | YES | 300
2 | 1.27 | 63 | 80.01 | 9.9 | 7.1 | 20.7256 | YES | 300
3 | 1.29 | 63 | 81.27 | 9.6 | 7 | 20.4578 | YES | 300
4 | 1.29 | 63 | 81.27 | 9.7 | 7.2 | 21.7973 | YES | 300
5 | 1.19 | 63 | 74.97 | 9 | 7.3 | 23.3831 | YES | 300
6 | 1.34 | 63 | 84.42 | 8.8 | 7.1 | 22.4586 | YES | 300
7 | 1.25 | 63 | 78.75 | 8.9 | 7.3 | 23.7001 | YES | 300
8 | 1.1 | 63 | 69.3 | 9.1 | 7.3 | 22.9922 | YES | 300
9 | 1.2 | 63 | 75.6 | 9.3 | 7.1 | 21.3894 | YES | 300
10 | 1.23 | 63 | 77.49 | 9 | 7.3 | 23.4896 | YES | 300
11 | 1.29 | 63 | 81.27 | 10.3 | 7.8 | 25.9055 | YES | 300
12 | 1.24 | 63 | 78.12 | 10.4 | 7.2 | 20.7005 | YES | 300
13 | 1.3 | 63 | 81.9 | 10.1 | 7.2 | 21.2549 | YES | 300
14 | 1.27 | 63 | 80.01 | 10.1 | 7 | 19.7564 | YES | 300
15 | 1.25 | 63 | 78.75 | 11 | 7 | 18.5936 | YES | 300
16 | 1.25 | 63 | 78.75 | 11.1 | 7 | 18.4738 | YES | 300
17 | 1.26 | 63 | 79.38 | 11.1 | 7 | 18.4942 | YES | 300
18 | 1.28 | 63 | 80.64 | 11.2 | 7.3 | 20.4331 | YES | 300
19 | 1.2 | 63 | 75.6 | 11.4 | 7.3 | 19.988 | YES | 300
20 | 1.26 | 63 | 79.38 | 11.9 | 7.1 | 18.178 | YES | 300
21 | 1.28 | 63 | 80.64 | 11.9 | 7.3 | 19.5207 | YES | 300
22 | 1.22 | 63 | 76.86 | 11.6 | 7.2 | 19.0996 | YES | 300
23 | 1.16 | 63 | 73.08 | 11.8 | 7.6 | 21.5247 | YES | 300
24 | 1.29 | 63 | 81.27 | 11.6 | 7.5 | 21.3691 | YES | 300
25 | 1.25 | 63 | 78.75 | 12.3 | 7.5 | 20.3189 | YES | 300
26 | 1.26 | 63 | 79.38 | 12.2 | 7 | 17.2307 | YES | 300
27 | 1.19 | 63 | 74.97 | 12.7 | 7.3 | 18.1307 | YES | 300
28 | 1.23 | 63 | 77.49 | 12.5 | 7.4 | 19.1503 | YES | 300
29 | 1.1 | 63 | 69.3 | 13 | 7.6 | 19.6508 | YES | 300
30 | 1.18 | 63 | 74.34 | 13.3 | 7.5 | 18.7352 | YES | 300
31 | 1.21 | 63 | 76.23 | 13.5 | 7.4 | 17.8788 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2