## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Douglas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-05-01
System Name: | City of Yoncalla |  |  | ID#: 41 00958 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | NIS | NIS | 0.066 | 0.064 | 0.067 | NIS | 0.07
2 | NIS | NIS | 0.06 | 0.068 | 0.075 | NIS | 0.08
3 | NIS | NIS | 0.063 | 0.07 | 0.088 | NIS | 0.09
4 | NIS | NIS | 0.064 | 0.074 | NIS | NIS | 0.07
5 | NIS | NIS | 0.078 | 0.074 | NIS | NIS | 0.08
6 | NIS | NIS | 0.062 | 0.068 | 0.07 | NIS | 0.07
7 | NIS | NIS | 0.066 | NIS | 0.07 | NIS | 0.07
8 | NIS | NIS | 0.059 | 0.039 | 0.037 | NIS | 0.06
9 | NIS | NIS | 0.029 | NIS | 0.027 | NIS | 0.03
10 | NIS | NIS | 0.036 | 0.037 | 0.037 | NIS | 0.04
11 | NIS | NIS | 0.038 | 0.042 | 0.048 | NIS | 0.05
12 | NIS | NIS | 0.046 | 0.048 | 0.046 | NIS | 0.05
13 | NIS | NIS | 0.088 | 0.051 | NIS | NIS | 0.09
14 | NIS | NIS | 0.048 | 0.051 | 0.055 | NIS | 0.06
15 | NIS | NIS | 0.053 | 0.054 | 0.062 | 0.06 | 0.06
16 | 0.05 | NIS | NIS | 0.051 | NIS | NIS | 0.05
17 | NIS | 0.05 | 0.057 | 0.063 | 0.06 | 0.07 | 0.07
18 | NIS | NIS | 0.061 | 0.052 | 0.069 | NIS | 0.07
19 | NIS | NIS | 0.06 | 0.058 | 0.053 | 0.064 | 0.06
20 | 0.06 | NIS | 0.07 | 0.053 | NIS | NIS | 0.07
21 | NIS | NIS | 0.049 | 0.061 | 0.059 | 0.06 | 0.06
22 | 0.07 | 0.06 | NIS | 0.052 | NIS | NIS | 0.07
23 | NIS | NIS | 0.062 | 0.046 | 0.045 | 0.06 | 0.06
24 | 0.05 | NIS | 0.045 | 0.059 | NIS | NIS | 0.06
25 | NIS | NIS | 0.054 | 0.044 | 0.049 | 0.049 | 0.05
26 | NIS | NIS | NIS | 0.038 | NIS | NIS | 0.04
27 | NIS | 0.04 | NIS | 0.042 | NIS | 0.05 | 0.05
28 | 0.05 | 0.05 | 0.05 | 0.049 | 0.048 | NIS | 0.05
29 | NIS | NIS | 0.042 | 0.046 | 0.055 | NIS | 0.06
30 | NIS | NIS | 0.056 | 0.043 | 0.045 | 0.04 | 0.06
31 | 0.05 | NIS | 0.038 | 0.043 | NIS | NIS | 0.05
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Anthony D. Rogers
[5 empty] | SIGNATURE: |  |  | DATE:6/3/2024
[5 empty] | PHONE #: ( 541 ) 459-7958 |  |  | CERT #:6714
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | City of Yoncalla |  | ID#: 41 00958 |  | Month/Year: | 2024-05-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.24 | 63 | 78.12 | 15.5 | 7 | 13.5368 | YES | 300
2 | 1.3 | 63 | 81.9 | 15.7 | 7 | 13.4487 | YES | 300
3 | 1.29 | 63 | 81.27 | 15.8 | 7 | 13.3436 | YES | 300
4 | 1.25 | 63 | 78.75 | 15.6 | 6.8 | 12.4957 | YES | 300
5 | 1.28 | 63 | 80.64 | 15.4 | 6.8 | 12.7082 | YES | 300
6 | 1.28 | 63 | 80.64 | 15.4 | 7 | 13.6902 | YES | 300
7 | 1.25 | 63 | 78.75 | 15.1 | 7 | 13.92 | YES | 300
8 | 1.2 | 63 | 75.6 | 15.3 | 7 | 13.6567 | YES | 300
9 | 1.17 | 63 | 73.71 | 15.5 | 7.5 | 16.1661 | YES | 300
10 | 1.14 | 63 | 71.82 | 15.8 | 7.1 | 13.6137 | YES | 300
11 | 1.06 | 63 | 66.78 | 16 | 7.1 | 13.3103 | YES | 300
12 | 1.13 | 63 | 71.19 | 16.8 | 7.6 | 15.313 | YES | 300
13 | 1.16 | 63 | 73.08 | 16.8 | 8 | 17.8158 | YES | 300
14 | 1.16 | 63 | 73.08 | 16.9 | 7.1 | 12.6752 | YES | 300
15 | 1.23 | 63 | 77.49 | 17.3 | 7.7 | 15.5458 | YES | 300
16 | 1.22 | 63 | 76.86 | 17.6 | 8.6 | 21.22 | YES | 300
17 | 1.05 | 63 | 66.15 | 17.7 | 8.7 | 21.4534 | YES | 300
18 | 1 | 63 | 63 | 18.2 | 8.5 | 19.1712 | YES | 300
19 | 1.01 | 63 | 63.63 | 18.4 | 8.4 | 18.2538 | YES | 300
20 | 1.16 | 63 | 73.08 | 18.3 | 8.5 | 19.393 | YES | 300
21 | 1.09 | 63 | 68.67 | 18.1 | 8.2 | 17.4537 | YES | 300
22 | 1.18 | 63 | 74.34 | 19.1 | 8.1 | 15.8983 | YES | 300
23 | 1.14 | 63 | 71.82 | 18.6 | 7.8 | 14.6409 | YES | 300
24 | 1.17 | 63 | 73.71 | 19 | 7.8 | 14.3036 | YES | 300
25 | 1.26 | 63 | 79.38 | 19.1 | 7.1 | 11.0585 | YES | 300
26 | 1.23 | 63 | 77.49 | 18.9 | 7.4 | 12.4942 | YES | 300
27 | 1.18 | 63 | 74.34 | 19.3 | 7.5 | 12.553 | YES | 300
28 | 1.22 | 63 | 76.86 | 20.2 | 8.1 | 14.8406 | YES | 300
29 | 1.23 | 63 | 77.49 | 19.6 | 7.5 | 12.3735 | YES | 300
30 | 1.26 | 63 | 79.38 | 19.6 | 7.9 | 14.4083 | YES | 300
31 | 1.22 | 63 | 76.86 | 19.7 | 7.8 | 13.7275 | YES | 300
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2